## Slide 1: ECEN 616, Fall 2022 Methods of Electric Power System Analysis
Prof. Adam Birchfield
Dept. of Electrical and Computer Engineering
Texas A&M University
abirchfield@tamu.edu
Class 15: Transmission Lines, Part 3

## Slide 2: Transmission Lines: Differential Section
Consider a two-terminal transmission line of length . Refer to the “sending end” as and the “receiving end” as . We’re interested in the sending and receiving end voltage and current, and
We define the distributed parameter line model as shown with
From circuit theory as

## Slide 3: Solving the Telegrapher’s Equations
These two equations are the telegrapher’s equations. We use the Fourier transform to convert time to frequency using the relation
where
where
The solutions have the general form in the frequency domain
Where and , and A and B are unknown constants
are all functions of frequency
Check that these solutions solve the differential equations

## Slide 4: Boundary Conditions
Eliminate A and B by solving for and , using the k and m terms defined on the prior page
After some algebra to eliminate A and B you get
Pause here. This is still an exact solution in the frequency domain, and we’ll come back here for frequency dependent models.
Remember and are functions of frequency

## Slide 5: Lossless Model in the Time Domain
For the lossless model, we assume , so and
So (which is a constant real number)
And , where
And for the equations we get
and
Convert to the time domain and get
where
where
This is exactly the lossless Bergeron model!

## Slide 6: Multiple Conductors
When we have multiple conductors, the frequency-domain telegrapher’s equations are still the same
and
But now, and are vectors of length , where is the number of conductors in the line (including neutral conductors and bundling)
And now and are matrices .
How do we handle this? Two parts:
  Eliminate conductors down to the main phases only
  Transform the phases into modes

## Slide 7: Eliminating Conductors
Eliminate conductors by making assumptions about the currents and voltages. For neutral conductors, for example, assume , so
and
Which leads to
Eliminating bundled conductors can be done in a similar way by assuming and

## Slide 8: Modal Transformations
The phase-to-phase matrices and (or and ), are in general unbalanced, non-diagonal matrices. If it were possible to transform these matrices into diagonal “mode” matrices and , we could solve each mode as a separate single-phase problem.
We do this using eigenvalue decomposition of the matrix , finding eigenvector matrix and diagonal eigenvalue matrix so that
Now we can find the mode voltages and currents
And the mode impedance matrices

## Slide 9: Modal Transformations, Cont.
How does the Modal transformation affect the telegrapher’s equations?
and
Now the equations become (verify)
and
BUT, the big difference is and are now diagonal matrices
So, each mode can be taken as a single phase separate problem. For mode ,
and

## Slide 10: Exactness of Modal Transformations
For completely transposed lines, modal transformation reduces to the method of symmetrical components
For other lines, the exact transformation matrix will depend on frequency.
For the constant parameter model (CP) we pick a frequency to design the model for, so we just use the modal transformation matrix associated with that frequency
For frequency dependent models, there are multiple options:
  Assume that the modal transformation matrix will still be a constant (though the individual modes will have frequency dependence)
  Advanced methods take into account frequency dependence of the modal transformation