## Slide 1: ECEN 616, Fall 2022 Methods of Electric Power System Analysis
Prof. Adam Birchfield
Dept. of Electrical and Computer Engineering
Texas A&M University
abirchfield@tamu.edu
Class 17: Transmission Lines, Part 5

## Slide 2: Frequency Dependence of Line Models
Even though the transformation matrix does depend on frequency, we will assume it can be treated as constant. Hence we have a set of independent single-phase “modes” of the form
Where and are complex nonlinear functions of frequency, making a direct conversion to time domain quite difficult
Mode-based frequency dependent (FD) models are based on approximating the effects of and that will be valid for many frequencies.
Key paper is J. R. Marti, “Accurate Modeling of FD Transmission Lines in EMT Simulations,” IEEE Trans. PAS, Jan. 1982

## Slide 3: Frequency Dependence of
The characteristic impedance depends on frequency for at least three reasons (1) (2) both R and L can vary with frequency due to skin effect (3) ground return effects are frequency dependent
is the current that would be present entering an equivalent circuit with a total impedance of that approximates
So the approach is to find such a network, where is close to across frequencies of interest
Rational fraction approximation
Where and are zeros and poles
Example Zc dependence on frequency

## Slide 4: Rational Function Approximation
A curve-fitting optimization is used to approximate with
So that we can replace our Bergeron model (which had a constant only to approximate ) with an equivalent RC network

## Slide 5: Frequency Dependence of
Looking at this equation again
Now that we have an approximation for how fits in, we need to know how to get values of the current source ()
Where is time delay of fastest component of
Now we convert to time domain and get a convolution
Because of the time delay , the integral only depends on historical values.
can be precalculated

## Slide 6: Reflection Coefficient
Recall the transmission line reflection coefficient, when a line with characteristic impedance is matched with an impedance
This means the reflected voltage that travels back will be
What does this mean about short circuit, open circuit, matched?
  Short circuit: reflected voltage wave exactly matches forward wave, . Current builds up and will be doubled.
What can we say about the current and any refracted voltage ?
1 2 3

## Slide 7: Lattice Diagrams
1 2 3
0

## Slide 8: Switching Surge Propagation Analysis
Diamond
Topaz
Emerald
Ruby
Sapphire
Switch location
(surge origin)
62 miles
48 miles
15 miles
50 miles
Wave Path | Time Delay
TD | 162
(TD)2 | 324
(TD)3 | 486
RD | 518
(TD)4 | 648
ED | 670
TDRD | 680
RDTD | 702
TSTD | 810
(TD)5 | 832
What will be the next surges to appear?
Remember different modes may have different propagation characteristics, and there will be frequency distortion and attenuation. Later surges may be smaller.

## Slide 9: Summary of Transmission Lines
Overhead and underground line characteristics and their relevance to calculating and matrices, frequency dependence
Numerical models for lossless, single-phase lines (Bergeron)
Adding losses to Bergeron model
Handling multiple conductor lines (elimination, modal analysis)
Frequency dependent line models
Analytical approximations: reflection coefficients, lattice diagrams, propagation analysis