## Slide 1: ECEN 616: Electromagnetic Transients in Power Systems
Adam Birchfield
Dept. of Electrical and Computer Engineering
Texas A&M University
abirchfield@tamu.edu
Solution to Example 8a

## Slide 2: Example 8a
A 15-km, single-phase transmission line is open on one end, and on the other end is terminated by a resistor. On the open end, a current pulse is injected, modeled as a double exponential with current , where , , and (this is a 0.5 characteristic lightning impulse). The line uses earth return and consists of a single conductor 1cm in diameter, 10m above the ground. Ignore sag and skin effect. In each of the following scenarios, calculate the maximum voltage on each end of the line:
a) Assuming a lossless earth and lossless transmission line, with a terminating impedance of 100 . Use the constant parameter (lossless Bergeron) line model evaluated at 60 Hz. Use EMTP to get the line constants, then solve the circuit both manually (using the programming environment of your choice) and in EMTP.

## Slide 3: Getting Line Parameters from EMTP
Line Data
  1 conductor: Phase 1, 0 resistance, 1cm diameter, 0 horizontal, 10 vertical, no sag or skin effect
  Model: constant parameter at 60 Hz
  Line length: 15 km and 0 ground return resistivity
  Generate data
Line model
  Load data from file
  R = 0

## Slide 4: Setting up the Equivalent Circuit
The line becomes two Norton sources, with resistance and current source and which depend on prior values on other end of the line
comes from double exponential equations and
is , the terminating impedance

## Slide 5: Setting up the Time Chart
0 |  |  |  |  |  |  | 
10 |  |  |  |  |  |  | 
20 |  |  |  |  |  |  | 
30 |  |  |  |  |  |  | 
40 |  |  |  |  |  |  | 
50 |  |  |  |  |  |  | 
60 |  |  |  |  |  |  | 
70 |  |  |  |  |  |  | 
80 |  |  |  |  |  |  | 
90 |  |  |  |  |  |  | 
100 |  |  |  |  |  |  | 
110 |  |  |  |  |  |  | 
120 |  |  |  |  |  |  | 
130 |  |  |  |  |  |  | 
140 |  |  |  |  |  |  | 
150 |  |  |  |  |  |  | 
0 |  |  |  |  |  |  | 
20 |  |  |  |  |  |  | 
30 |  |  |  |  |  |  | 
40 |  |  |  |  |  |  | 
50 |  |  |  |  |  |  | 
60 |  |  |  |  |  |  | 
70 |  |  |  |  |  |  | 
80 |  |  |  |  |  |  | 
90 |  |  |  |  |  |  | 
100 |  |  |  |  |  |  | 
110 |  |  |  |  |  |  | 
120 |  |  |  |  |  |  | 
130 |  |  |  |  |  |  | 
140 |  |  |  |  |  |  | 
150 |  |  |  |  |  |  | 
Chooose as for hand example
(in your actual code use a much smaller time step, 0.1 should do.)

## Slide 6: Initial Values
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 |  |  |  |  |  |  | 
20 |  |  |  |  |  |  | 
30 |  |  |  |  |  |  | 
40 |  |  |  |  |  |  | 
50 |  |  |  |  |  |  | 
60 |  |  |  |  |  |  | 
70 |  |  |  |  |  |  | 
80 |  |  |  |  |  |  | 
90 |  |  |  |  |  |  | 
100 |  |  |  |  |  |  | 
110 |  |  |  |  |  |  | 
120 |  |  |  |  |  |  | 
130 |  |  |  |  |  |  | 
140 |  |  |  |  |  |  | 
150 |  |  |  |  |  |  | 
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 |  |  |  |  |  |  | 
30 |  |  |  |  |  |  | 
40 |  |  |  |  |  |  | 
50 |  |  |  |  |  |  | 
60 |  |  |  |  |  |  | 
70 |  |  |  |  |  |  | 
80 |  |  |  |  |  |  | 
90 |  |  |  |  |  |  | 
100 |  |  |  |  |  |  | 
110 |  |  |  |  |  |  | 
120 |  |  |  |  |  |  | 
130 |  |  |  |  |  |  | 
140 |  |  |  |  |  |  | 
150 |  |  |  |  |  |  | 
Assume the line is initially unloaded

## Slide 7: Surge Current
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5313 A |  |  |  |  |  | 
20 | 2639 |  |  |  |  |  | 
30 | 1310 |  |  |  |  |  | 
40 | 651 |  |  |  |  |  | 
50 | 323 |  |  |  |  |  | 
60 | 160 |  |  |  |  |  | 
70 | 80 |  |  |  |  |  | 
80 | 40 |  |  |  |  |  | 
90 | 20 |  |  |  |  |  | 
100 | 10 |  |  |  |  |  | 
110 | 5 |  |  |  |  |  | 
120 | 2 |  |  |  |  |  | 
130 | 1 |  |  |  |  |  | 
140 | 1 |  |  |  |  |  | 
150 | 0 |  |  |  |  |  | 
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
 | 5313 A |  |  |  |  |  | 
20 | 2639 |  |  |  |  |  | 
30 | 1310 |  |  |  |  |  | 
40 | 651 |  |  |  |  |  | 
50 | 323 |  |  |  |  |  | 
60 | 160 |  |  |  |  |  | 
70 | 80 |  |  |  |  |  | 
80 | 40 |  |  |  |  |  | 
90 | 20 |  |  |  |  |  | 
100 | 10 |  |  |  |  |  | 
110 | 5 |  |  |  |  |  | 
120 | 2 |  |  |  |  |  | 
130 | 1 |  |  |  |  |  | 
140 | 1 |  |  |  |  |  | 
150 | 0 |  |  |  |  |  | 
Surge current is just a function of and does not depend on the rest of the circuit. Use the equation

## Slide 8: First Time Step
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5313 A | 0 | 0 | 2614 kV | 0 | 5313 A | 0
20 | 2639 |  |  |  |  |  | 
30 | 1310 |  |  |  |  |  | 
40 | 651 |  |  |  |  |  | 
50 | 323 |  |  |  |  |  | 
60 | 160 |  |  |  |  |  | 
70 | 80 |  |  |  |  |  | 
80 | 40 |  |  |  |  |  | 
90 | 20 |  |  |  |  |  | 
100 | 10 |  |  |  |  |  | 
110 | 5 |  |  |  |  |  | 
120 | 2 |  |  |  |  |  | 
130 | 1 |  |  |  |  |  | 
140 | 1 |  |  |  |  |  | 
150 | 0 |  |  |  |  |  | 
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
 | 5313 A | 0 | 0 | 2614 kV | 0 | 5313 A | 0
20 | 2639 |  |  |  |  |  | 
30 | 1310 |  |  |  |  |  | 
40 | 651 |  |  |  |  |  | 
50 | 323 |  |  |  |  |  | 
60 | 160 |  |  |  |  |  | 
70 | 80 |  |  |  |  |  | 
80 | 40 |  |  |  |  |  | 
90 | 20 |  |  |  |  |  | 
100 | 10 |  |  |  |  |  | 
110 | 5 |  |  |  |  |  | 
120 | 2 |  |  |  |  |  | 
130 | 1 |  |  |  |  |  | 
140 | 1 |  |  |  |  |  | 
150 | 0 |  |  |  |  |  | 
Assume that voltages and currents have been 0 for negative time, so historical values are 0.
Because right hand side current source is 0 , the current and voltage there will be 0 as well.

## Slide 9: Time Steps 20-50
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5313 A | 0 | 0 | 2614 kV | 0 | 5313 A | 0
20 | 2639 | 0 | 0 | 1311 | 0 | 2639 | 0
30 | 1310 | 0 | 0 | 651 | 0 | 1310 | 0
40 | 651 | 0 | 0 | 323 | 0 | 651 | 0
50 | 323 | 0 | 0 | 161 | 0 | 323 | 0
60 | 160 |  |  |  |  |  | 
70 | 80 |  |  |  |  |  | 
80 | 40 |  |  |  |  |  | 
90 | 20 |  |  |  |  |  | 
100 | 10 |  |  |  |  |  | 
110 | 5 |  |  |  |  |  | 
120 | 2 |  |  |  |  |  | 
130 | 1 |  |  |  |  |  | 
140 | 1 |  |  |  |  |  | 
150 | 0 |  |  |  |  |  | 
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
 | 5313 A | 0 | 0 | 2614 kV | 0 | 5313 A | 0
20 | 2639 | 0 | 0 | 1311 | 0 | 2639 | 0
30 | 1310 | 0 | 0 | 651 | 0 | 1310 | 0
40 | 651 | 0 | 0 | 323 | 0 | 651 | 0
50 | 323 | 0 | 0 | 161 | 0 | 323 | 0
60 | 160 |  |  |  |  |  | 
70 | 80 |  |  |  |  |  | 
80 | 40 |  |  |  |  |  | 
90 | 20 |  |  |  |  |  | 
100 | 10 |  |  |  |  |  | 
110 | 5 |  |  |  |  |  | 
120 | 2 |  |  |  |  |  | 
130 | 1 |  |  |  |  |  | 
140 | 1 |  |  |  |  |  | 
150 | 0 |  |  |  |  |  | 
Assume that voltages and currents have been 0 for negative time, so historical values are 0. For time step , historical values are zero as well.
Because right hand side current source is 0 , the current and voltage there will be 0 as well.

## Slide 10: Time Step 60
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5313 A | 0 | 0 | 2614 kV | 0 | 5313 A | 0
20 | 2639 | 0 | 0 | 1311 | 0 | 2639 | 0
30 | 1310 | 0 | 0 | 651 | 0 | 1310 | 0
40 | 651 | 0 | 0 | 323 | 0 | 651 | 0
50 | 323 | 0 | 0 | 161 | 0 | 323 | 0
60 | 160 | 0 | -10627 A | 80 | 885 | 160 | -8850 A
70 | 80 |  |  |  |  |  | 
80 | 40 |  |  |  |  |  | 
90 | 20 |  |  |  |  |  | 
100 | 10 |  |  |  |  |  | 
110 | 5 |  |  |  |  |  | 
120 | 2 |  |  |  |  |  | 
130 | 1 |  |  |  |  |  | 
140 | 1 |  |  |  |  |  | 
150 | 0 |  |  |  |  |  | 
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
 | 5313 A | 0 | 0 | 2614 kV | 0 | 5313 A | 0
20 | 2639 | 0 | 0 | 1311 | 0 | 2639 | 0
30 | 1310 | 0 | 0 | 651 | 0 | 1310 | 0
40 | 651 | 0 | 0 | 323 | 0 | 651 | 0
50 | 323 | 0 | 0 | 161 | 0 | 323 | 0
60 | 160 | 0 | -10627 A | 80 | 885 | 160 | -8850 A
70 | 80 |  |  |  |  |  | 
80 | 40 |  |  |  |  |  | 
90 | 20 |  |  |  |  |  | 
100 | 10 |  |  |  |  |  | 
110 | 5 |  |  |  |  |  | 
120 | 2 |  |  |  |  |  | 
130 | 1 |  |  |  |  |  | 
140 | 1 |  |  |  |  |  | 
150 | 0 |  |  |  |  |  | 
Surge has reached the other side!
()
()

## Slide 11: Time Steps 70-100
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5313 A | 0 | 0 | 2614 kV | 0 | 5313 A | 0
20 | 2639 | 0 | 0 | 1311 | 0 | 2639 | 0
30 | 1310 | 0 | 0 | 651 | 0 | 1310 | 0
40 | 651 | 0 | 0 | 323 | 0 | 651 | 0
50 | 323 | 0 | 0 | 161 | 0 | 323 | 0
60 | 160 | 0 | -10627 A | 80 | 885 | 160 | -8850 A
70 | 80 | 0 | -5277 | 40 | 439 | 80 | -4393
80 | 40 | 0 | -2621 | 20 | 218 | 40 | -2181
90 | 20 | 0 | -1301 | 10 | 108 | 20 | -1083
100 | 10 | 0 | -646 | 5 | 54 | 10 | -538
110 | 5 |  |  |  |  |  | 
120 | 2 |  |  |  |  |  | 
130 | 1 |  |  |  |  |  | 
140 | 1 |  |  |  |  |  | 
150 | 0 |  |  |  |  |  | 
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
 | 5313 A | 0 | 0 | 2614 kV | 0 | 5313 A | 0
20 | 2639 | 0 | 0 | 1311 | 0 | 2639 | 0
30 | 1310 | 0 | 0 | 651 | 0 | 1310 | 0
40 | 651 | 0 | 0 | 323 | 0 | 651 | 0
50 | 323 | 0 | 0 | 161 | 0 | 323 | 0
60 | 160 | 0 | -10627 A | 80 | 885 | 160 | -8850 A
70 | 80 | 0 | -5277 | 40 | 439 | 80 | -4393
80 | 40 | 0 | -2621 | 20 | 218 | 40 | -2181
90 | 20 | 0 | -1301 | 10 | 108 | 20 | -1083
100 | 10 | 0 | -646 | 5 | 54 | 10 | -538
110 | 5 |  |  |  |  |  | 
120 | 2 |  |  |  |  |  | 
130 | 1 |  |  |  |  |  | 
140 | 1 |  |  |  |  |  | 
150 | 0 |  |  |  |  |  | 
= 0 ()
()

## Slide 12: Time Step 110
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5313 A | 0 | 0 | 2614 kV | 0 | 5313 A | 0
20 | 2639 | 0 | 0 | 1311 | 0 | 2639 | 0
30 | 1310 | 0 | 0 | 651 | 0 | 1310 | 0
40 | 651 | 0 | 0 | 323 | 0 | 651 | 0
50 | 323 | 0 | 0 | 161 | 0 | 323 | 0
60 | 160 | 0 | -10627 A | 80 | 885 kV | 160 | -8850 A
70 | 80 | 0 | -5277 | 40 | 439 | 80 | -4393
80 | 40 | 0 | -2621 | 20 | 218 | 40 | -2181
90 | 20 | 0 | -1301 | 10 | 108 | 20 | -1083
100 | 10 | 0 | -646 | 5 | 54 | 10 | -538
110 | 5 | 7067 A | -320 | -3510 | 27 | 5 | -267
120 | 2 |  |  |  |  |  | 
130 | 1 |  |  |  |  |  | 
140 | 1 |  |  |  |  |  | 
150 | 0 |  |  |  |  |  | 
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
 | 5313 A | 0 | 0 | 2614 kV | 0 | 5313 A | 0
20 | 2639 | 0 | 0 | 1311 | 0 | 2639 | 0
30 | 1310 | 0 | 0 | 651 | 0 | 1310 | 0
40 | 651 | 0 | 0 | 323 | 0 | 651 | 0
50 | 323 | 0 | 0 | 161 | 0 | 323 | 0
60 | 160 | 0 | -10627 A | 80 | 885 kV | 160 | -8850 A
70 | 80 | 0 | -5277 | 40 | 439 | 80 | -4393
80 | 40 | 0 | -2621 | 20 | 218 | 40 | -2181
90 | 20 | 0 | -1301 | 10 | 108 | 20 | -1083
100 | 10 | 0 | -646 | 5 | 54 | 10 | -538
110 | 5 | 7067 A | -320 | -3510 | 27 | 5 | -267
120 | 2 |  |  |  |  |  | 
130 | 1 |  |  |  |  |  | 
140 | 1 |  |  |  |  |  | 
150 | 0 |  |  |  |  |  | 
Return surge has gotten back to the sending end
()
()

## Slide 13: Time Steps 120-150
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 5313 A | 0 | 0 | 2614 kV | 0 | 5313 A | 0
20 | 2639 | 0 | 0 | 1311 | 0 | 2639 | 0
30 | 1310 | 0 | 0 | 651 | 0 | 1310 | 0
40 | 651 | 0 | 0 | 323 | 0 | 651 | 0
50 | 323 | 0 | 0 | 161 | 0 | 323 | 0
60 | 160 | 0 | -10627 A | 80 | 885 kV | 160 | -8850 A
70 | 80 | 0 | -5277 | 40 | 439 | 80 | -4393
80 | 40 | 0 | -2621 | 20 | 218 | 40 | -2181
90 | 20 | 0 | -1301 | 10 | 108 | 20 | -1083
100 | 10 | 0 | -646 | 5 | 54 | 10 | -538
110 | 5 | 7067 A | -320 | -3510 | 27 | 5 | -267
120 | 2 | 3509 | -159 | -1743 | 13 | 2 | -133
130 | 1 | 1743 | -79 | -866 | 7 | 1 | -66
140 | 1 | 865 | -39 | -430 | 3 | 1 | -33
150 | 0 | 430 | -20 | -213 | 2 | 0 | -16
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
 | 5313 A | 0 | 0 | 2614 kV | 0 | 5313 A | 0
20 | 2639 | 0 | 0 | 1311 | 0 | 2639 | 0
30 | 1310 | 0 | 0 | 651 | 0 | 1310 | 0
40 | 651 | 0 | 0 | 323 | 0 | 651 | 0
50 | 323 | 0 | 0 | 161 | 0 | 323 | 0
60 | 160 | 0 | -10627 A | 80 | 885 kV | 160 | -8850 A
70 | 80 | 0 | -5277 | 40 | 439 | 80 | -4393
80 | 40 | 0 | -2621 | 20 | 218 | 40 | -2181
90 | 20 | 0 | -1301 | 10 | 108 | 20 | -1083
100 | 10 | 0 | -646 | 5 | 54 | 10 | -538
110 | 5 | 7067 A | -320 | -3510 | 27 | 5 | -267
120 | 2 | 3509 | -159 | -1743 | 13 | 2 | -133
130 | 1 | 1743 | -79 | -866 | 7 | 1 | -66
140 | 1 | 865 | -39 | -430 | 3 | 1 | -33
150 | 0 | 430 | -20 | -213 | 2 | 0 | -16
()
()

## Slide 14: Results with
Surge doesn’t get to the other end until 500th time step, doesn’t return until the 1000th
Can now see the rise and fall of the pulse, capture true peak

## Slide 15: EMTP Results