## Slide 1: ECEN 616, Fall 2022 Electromagnetic Transients in Power Systems
Prof. Adam Birchfield
Dept. of Electrical and Computer Engineering
Texas A&M University
abirchfield@tamu.edu
Class 24: Lightning Studies

## Slide 2: What is the Frequency, Peak Voltage, and Energy Discharge in a Typical Lightning Strike?
1 Hz
10 Hz
100 Hz
1 kHz
10 kHz
100 kHz
1 MHz
10 MHz
100 MHz
1 GHz
10 GHz
100 GHz
1 V
10 V
100 V
1 kV
10 kV
100 kV
1 MV
10 MV
100 MV
1 GV
10 GV
100 GV
1 Wh
10 Wh
100 Wh
1 kWh
10 kWh
100 kWh
1 MWh
10 MWh
100 MWh
1 GWh
10 GWh
100 GWh

## Slide 3: Lightning Safety
Lightning strikes have randomness about them, and can occur as far as 10 miles from rainfall
If you hear thunder or see lightning, get immediately to a safe place, such as inside a fully enclosed building or metal vehicle
If a lightning strike gets onto a metal pipe or wiring system, it can travel long distances, including into buildings
  Stay away from corded electrical equipment, showers, baths, and sinks, during a thunderstorm
  Unplug sensitive electronics or use surge protective devices
What state had the most lightning strikes per square mile in 2021?

## Slide 4: Effect of Lightning on a Power System
Direct lightning stroke to equipment
Direct lightning stroke to phase conductor
Lightning stroke to shield or ground wire
Lightning stroke to transmission tower
  Backflashover if the tower potential gets too high
Lightning stroke to ground in vicinity of phase conductors

## Slide 5: Modeling a Lightning-Induced Surge
Basic Impulse Level (BIL) tests involve the current surge of a 1.2/50 waveshape. This waveshape has a rise time of 1.2 and a fall time (to 50%) of 50
It can be represented with a double exponential
Where and
There is also an 8/20us waveform

## Slide 6: Shielding
Shield wires are grounded conductors placed above the phase conductors to reduce the chance of direct strikes to the phase conductors
How many and where to place them is shielding design

## Slide 7: Surge Arresters
When an overvoltage surge approaches a surge arrestor, ideally the device should clamp the system voltage to its nominal value, avoiding flashover and damage to equipment
  Including lightning, switching surges, etc.
Technologies
  Rod gap: when voltage exceeds air breakdown voltage, an arc forms
  Silicon carbide
  Medal-oxide
Modeled with nonlinear resistors