## Slide 1: ECEN 460, Spring 2023 Power System Operation and Control
Prof. Adam Birchfield
Dept. of Electrical and Computer Engineering
Texas A&M University
abirchfield@tamu.edu
Class 5: Transformers, Part 1

## Slide 2: Homework 3 and 4
No homework on generators. Make sure you understand the lecture notes and labs 3 and 4 (starting next week).
Homework 3 on transformers: book problems 3.4, 3.23, due Feb. 7th.
Homework 4 on transmission lines: book regular problems 4.10, 4.11, 4.20, and 4.41, 5.14 (a,b), 5.38, and 5.41 (a,b), due Feb. 14th.

## Slide 3: Transformers Overview
Power systems are characterized by many different voltage levels, ranging from 765 kV down to 240/120 volts.
Transformers are used to transfer power between different voltage levels.
The ability to inexpensively change voltage levels is a key advantage of ac systems over dc systems.
In this section we’ll development models for the transformer and discuss various ways of connecting three phase transformers.

## Slide 4: Transmission Level Transformer

## Slide 5: Ideal Transformer
First, we review the voltage/current relationships for an ideal transformer
  no real power losses
  magnetic core has infinite permeability
  no leakage flux
We’ll define the “primary” side of the transformer as the side that usually takes power, and the secondary as the side that usually delivers power.
  primary is usually the side with the higher voltage but may be the low voltage side on a generator step-up transformer.

## Slide 6: XF Theory

## Slide 7: Ideal Transformer Relationships

## Slide 8: Current and Voltage Relationships

## Slide 9: Impedance Transformation Example
Example: Calculate the primary voltage and current for an impedance load on the secondary

## Slide 10: Real Transformers
Real transformers
  have losses
  have leakage flux
  have finite permeability of magnetic core
Real power losses
  resistance in windings (i2 R)
  core losses due to eddy currents and hysteresis

## Slide 11: Transformer Core Losses
Eddy currents arise because of changing flux in core.
Eddy currents are reduced by laminating the core
Hysteresis losses are proportional to area of BH curve and the frequency
These losses are reduced by using material with a thin BH curve
No lamination, high eddy current
With lamination, low eddy current

## Slide 12: Simplified Equivalent Circuit
Often the shunt elements are assumed to have such high impedance that they are ignored

## Slide 13: Calculation of Model Parameters
The parameters of the model are determined based upon
  nameplate data: gives the rated voltages and power
  open circuit test: rated voltage is applied to primary with secondary open; measure the primary current and losses (the test may also be done applying the voltage to the secondary, calculating the values, then referring the values back to the primary side).
  short circuit test: with secondary shorted, apply voltage to primary to get rated current to flow; measure voltage and losses.

## Slide 14: Transformer Example
Example: A single phase, 100 MVA, 200/80 kV transformer has the following test data:
open circuit: 20 amps, with 10 kW losses
short circuit: 30 kV, with 500 kW losses
Determine the model parameters.

## Slide 15: Transformer Example, Cont’d
From the short circuit test
From the open circuit test

## Slide 16: Residential Distribution Transformers
Single phase transformers are commonly used in residential distribution systems. Most distribution systems are 4 wire, with a multi-grounded, common neutral.
Image: www.osha.gov/dte/library/electrical/electrical_10.gif

## Slide 17: How Do We Deal with Transformers on a Large System?
With many transformers, the equations of the form v1=a*v2 would be everywhere
The per-unit system was designed to make hand calculations and early computer calculations easier.
  Divide all numerical values by a "base" value, i.e., normalize them
  Instead of voltages in V, currents in A, impedance in Ohms, all are given in per-unit.
  Ideal transformers go away in the per-unit system
  Per-unit system has other advantages as well, and is extremely common in industry
  Next lecture we will discuss the per-unit system in detail

## Slide 18: Per Unit Calculations
A key problem in analyzing power systems is the large number of transformers.
  It would be very difficult to continually have to refer impedances to the different sides of the transformers
This problem is avoided by a normalization of all variables.
This normalization is known as per unit analysis.

## Slide 19: Per Unit Conversion Procedure, Single-Phase
Pick a single-phase VA base for the entire system,
Pick a voltage base for each different voltage level, . Voltage bases are related by transformer turns ratios. Voltages are line to neutral.
Calculate the impedance base,
Calculate the current base,
Convert actual values to per unit
Note, per unit conversion on affects magnitudes, not
the angles. Also, per unit quantities no longer have
units (i.e., a voltage is 1.0 p.u., not 1 p.u. volts)

## Slide 20: Per Unit Solution Procedure
Convert to per unit (p.u.) (many problems are already in per unit)
Solve
Convert back to actual as necessary

## Slide 21: Per Unit Example
Solve for the current, load voltage and load power in the circuit shown below using per unit analysis with an SB of 100 MVA, and voltage bases of 8 kV, 80 kV and 16 kV.
Original Circuit

## Slide 22: Per Unit Example, Cont’d
Same circuit, with
values expressed
in per unit.

## Slide 23: Per Unit Example, Cont’d

## Slide 24: Per Unit Example, Cont’d
To convert back to actual values just multiply the
per unit values by their per unit base

## Slide 25: Three Phase Per-Unit
Procedure is very similar to 1 phase except we use a 3 phase VA base, and use line to line voltage bases
Pick a 3f VA base for the entire system
Pick a voltage base for each different voltage level, VB. Voltages are line to line.
Calculate the impedance base
Exactly the same impedance bases as with single phase!

## Slide 26: Three Phase Per-Unit, Cont'd
Calculate the current base,
Convert actual values to per unit
Exactly the same current bases as with single phase!
But, be careful in using 3ph bases to calculate it (need a root 3)