## Slide 1: ECEN 460, Spring 2023 Power System Operation and Control
Prof. Adam Birchfield
Dept. of Electrical and Computer Engineering
Texas A&M University
abirchfield@tamu.edu
Class 6: Transformers, Part 2

## Slide 2: Homework 3 and 4
No homework on generators. Make sure you understand the lecture notes and labs 3 and 4 (starting next week).
Homework 3 on transformers: book problems 3.4, 3.23, due Feb. 7th.
Homework 4 on transmission lines: book regular problems 4.10, 4.11, 4.20, and 4.41, 5.14 (a,b), 5.38, and 5.41 (a,b), due Feb. 14th.

## Slide 3: Three Phase Per-Unit
Procedure is very similar to 1 phase except we use a 3 phase VA base, and use line to line voltage bases
Pick a VA base for the entire system
Pick a voltage base for each different voltage level, . Voltages are line to line.
Calculate the impedance base
Exactly the same impedance bases as with single phase!

## Slide 4: Three Phase Per-Unit, Cont'd
Calculate the current base,
Convert actual values to per unit
Exactly the same current bases as with single phase!
But, be careful in using 3ph bases to calculate it (need a root 3)

## Slide 5: Three Phase Per-Unit Example
Solve for the current, load voltage and load power in the previous circuit, assuming a power base of 300 MVA, and line to line voltage bases of 13.8 kV,138 kV and 27.6 kV (square root of 3 larger than the 1f example voltages). Also assume the generator is Y-connected so its line to line voltage is 13.8 kV.
Convert to per unit
as before. Note the
system is exactly the
same!

## Slide 6: 3 Per-Unit Example, Cont'd
Again, analysis is exactly the same!

## Slide 7: 3 Per-Unit Example, Cont'd
Differences appear when we convert back to actual values

## Slide 8: 3 Per-Unit Example 2
Assume a load of 100+j50 MVA with of 69 kV is connected to a source through the below network:
What is the supply current and complex power?
Answer: I=467 amps, S = 103.3 + j76.0 MVA

## Slide 9: Per Unit Change of MVA Base
Parameters for equipment are often given using power rating of equipment as the MVA base
To analyze a system all per unit data must be on a common power base

## Slide 10: Per Unit Change of Base Example
A 54 MVA transformer has a leakage reactance of 3.69%. What is the reactance on a 100 MVA base?

## Slide 11: Transformer Reactance
Transformer reactance is often specified as a percentage, say 10%. This is a per unit value (divide by 100) on the power base of the transformer.
Example: A 350 MVA, 230/20 kV transformer has leakage reactance of 10%. What is p.u. value on 100 MVA base? What is value in ohms (230 kV)?

## Slide 12: Three Phase Transformers
There are 4 different ways to connect 3 transformers: Y-Y, D-D, Y-D, D-Y
  The reasons have to do with grounding and harmonics, which are outside of the ECEN 460 scope
  Only Y connections can be grounded
  Mixing Y and D introduces a 30-degree phase shift
Most high voltage generator step-up transformers (GSUs) are D on the generator side, grounded Y on the transmission side
Most transmission to distribution is D on the transmission side, grounded Y on the distribution side

## Slide 13: Autotransformers
Autotransformers are transformers in which the primary and secondary windings are coupled magnetically and electrically.
This results in lower cost, and smaller size and weight.
Most transmission level transformers are autotransformers, connected Y-Y with the low side grounded
The key disadvantage is loss of electrical isolation between the voltage levels; not used when a is large. For example, in stepping down 7160/240 V we do not ever want 7160 on the low side!

## Slide 14: Three Winding Transformers
Many high voltage transformers have a third winding, called the tertiary winding; called three winding transformers
There are a number of benefits in having 3 windings
  Tertiary can be used to provide lower voltage electric service, including providing substation service for remote transmission substations; sometimes capacitors are connected to the tertiary
  Helps with fault protection by reducing the zero sequence current providing higher zero sequence currents (beyond ECEN 460 scope)
  When D-connected helps to reduce unbalanced and third harmonic issues (again beyond ECEN 460 scope)

## Slide 15: Load Tap-Changing Transformers
LTC transformers have tap ratios that can be varied to regulate bus voltages
  Sometimes called on-load tap-changing transformers (OLTCs) or under-load tap-changing transformers (ULTCs)
The typical range of variation is 10% from the nominal values, usually in 33 discrete steps (0.0625% per step).
Because tap changing is a mechanical process, LTC transformers usually have a time delay deadband to avoid repeated changes (e.g., 30 seconds)
Unbalanced tap positions can cause “circulating vars”

## Slide 16: LTCs and Circulating Vars

## Slide 17: Phase Shifting Transformers
Phase shifting transformers are used to control the phase angle across the transformer
  Also called phase angle regulators (PARs) or quadrature booster transformers (British usage)
Since power flow through the transformer depends upon phase angle, this allows the transformer to regulate the power flow through the transformer
Phase shifters can be used to prevent inadvertent "loop flow" and to prevent line overloads.
Image Source: en.wikipedia.org/wiki/Quadrature_booster#/media/File:Qb-3ph.svg

## Slide 18: Phase Shifter Example 3.13

## Slide 19: Phase Shifter Example: Lake Erie Loop Flow
There are five phase shifters (called phase angle regulators [PARs] here) at the border between Michigan and Ontario. They are used to control how much electricity travels between the US and Canada
By adjusting the PARs, the flow of electricity that “loops” around Lake Erie can be controlled
Source: MISO Board of Directors Market Committee Update, 9/30/13