## Slide 1: ECEN 460, Spring 2023 Power System Operation and Control
Prof. Adam Birchfield
Dept. of Electrical and Computer Engineering
Texas A&M University
abirchfield@tamu.edu
Class 22: Exciter and Governor Controls

## Slide 2: Class Outline
Review of three-phase AC power calculations
Structure, history, and design of power systems
Generator and load modeling
Transmission line and transformer modeling
The power flow problem and solution methods
Economic power system operation
Dynamics and stability of power systems
Emerging topics
✔
✔
✔
✔
✔
✔
➔
Exam 2 will focus on these topics
Tuesday, April 18
A bit more conceptual material between Exam 2 and the final

## Slide 3: Exam 2 – Tuesday April 18th
Conceptual questions:
  Newton-Raphson Power flow
  Power flow approximations (such as DC power flow)
  Large power system operations (such as the 24 statements)
  Power system economics (economic dispatch, OPF, SCOPF, markets)
  Dynamics and stability. No problems related to dynamics for Exam 2, but the Final will likely have a dynamics problem.
One problem related to power flow (including full Newton-Raphson power flow and/or DC power flow)
One problem related to economic dispatch

## Slide 4: Undergraduate Research Opportunities
If you’re interested in doing undergraduate research, let me know!
There are paid and class credit opportunities available (summer and semester)
What is research? Developing new methods and technologies to make the world a better place
  No prior research experience needed
Great way to find out if grad school might be right for you

## Slide 5: Graduate School
Build on your undergrad degree with advanced courses and research
Masters – about 2 years
PhD – Typically 4-5 years working toward specific expertise
Many funding sources available – Research/Teaching assistantship, internal/external fellowships
78 faculty members from 7 broad areas of research expertise
If you are interested in it, particularly in the power systems area, let me know!
For more information, see the ECEN graduate student handbook
https://engineering.tamu.edu/electrical/_files/_documents/_content-documents/ECEN-Grad-Handbook-2022-2023-30Aug2022.pdf

## Slide 6: The Generator Dynamic Equations We Will Use
Example power system problem with differential algebraic equations (DAEs) is the classical synchronous generator connected to an infinite bus.
The two differential variables are and ; in practice dynamic models can have many more.
Generator Parameters
is the machine inertia constant (in seconds)
is the synchronous frequency (260)
is the mechanical torque (power being supplied by the prime mover)
is the generator internal voltage, as controlled by the excitation system
is the generator transient impedance
damping constant of the generator
Infinite Bus / System
The infinite bus is defined by a Thevenin equivalent with voltage
And reactance
These are the harder variables to get.

## Slide 7: Handout from Last Class
A 60 Hz generator is supplying 200 MW and 0 Mvar to an infinite bus (with 1.0 per-unit) through two parallel transmission lines. Each transmission line has a per-unit impedance (with 100 MVA base) of j0.04. The per-unit transient reactance for the machine is j0.03, and its inertia constant is 10 seconds. (No damping.) A fault occurs at time = 0 halfway down one of the lines.
Rewrite the equations above with the only remaining variables: , , , , , and .
Draw a circuit diagram of the system (a) before the fault and (b) during the fault. Use this to calculate the Thevenin equivalent impedance for each condition.
The pre-fault condition is in steady-state. Calculate the internal voltage, which will be equal to . What are the constant values of and , and the initial values of the variables and ?
Use Euler’s method with a time step of seconds, find the value of and at and .

## Slide 8
Euler’s method
Where
A 60 Hz generator is supplying 200 MW and 0 Mvar to an infinite bus (with 1.0 per-unit) through two parallel transmission lines. Each transmission line has a per-unit impedance (with 100 MVA base) of j0.04. The per-unit transient reactance for the machine is j0.03, and its inertia constant is 10 seconds. (No damping.) A fault occurs at time = 0 halfway down one of the lines.
Before the fault
The generator is connected to a Thevenin equivalent with
Solve the circuit for the generator internal voltage,
Which will give you and initial value of :
Now consider steady-state, to get
And
After the fault
The Thevenin equivalent changes. Find the open circuit voltage and equivalent impedance
Now rewrite the swing equation
1
+
_
E
+
_
Initial conditions:
1
+
_
E
+
_
j0.03
j0.04
j0.04
j0.03
j0.04
j0.02
j0.02

## Slide 9: Handout from Last Class – Solution
t |  |  |  | 
0 | 0.0997 | 0 | 0 | 23.32872
0.01 | 0.0997 | 0.233287 | 0.233287 | 23.32872
0.02 | 0.102033 | 0.466574 | 0.466574 | 22.99362
0.03 | 0.106699 | 0.696511 | 0.696511 | 22.32367
0.04 | 0.113664 | 0.919747 | 0.919747 | 21.32418
0.05 | 0.122861 | 1.132989 | 1.132989 | 20.00557
0.06 | 0.134191 | 1.333045 | 1.333045 | 18.38331
0.07 | 0.147522 | 1.516878 | 1.516878 | 16.4778
0.08 | 0.16269 | 1.681656 | 1.681656 | 14.31411
0.09 | 0.179507 | 1.824797 | 1.824797 | 11.92169
0.1 | 0.197755 | 1.944014 | 1.944014 | 9.333903
t |  |  |  | 
0 | 0.0997 | 0 | 0 | 23.32872
0.01 | 0.0997 | 0.233287 | 0.233287 | 23.32872
0.02 | 0.102033 | 0.466574 | 0.466574 | 22.99362
0.03 | 0.106699 | 0.696511 | 0.696511 | 22.32367
0.04 | 0.113664 | 0.919747 | 0.919747 | 21.32418
0.05 | 0.122861 | 1.132989 | 1.132989 | 20.00557
0.06 | 0.134191 | 1.333045 | 1.333045 | 18.38331
0.07 | 0.147522 | 1.516878 | 1.516878 | 16.4778
0.08 | 0.16269 | 1.681656 | 1.681656 | 14.31411
0.09 | 0.179507 | 1.824797 | 1.824797 | 11.92169
0.1 | 0.197755 | 1.944014 | 1.944014 | 9.333903

## Slide 10: Homework
Keep working through handout, including practice problems:
More practice for Euler’s method: calculate the first three time steps of each initial value problem.
1.
2.
3.
Use the swing equation from before:
A 60 Hz generator is supplying 150 MW and 0 Mvar to an infinite bus (with 1.0 per-unit) through two parallel transmission lines. The per-unit transient reactance for the machine is j0.01, and its inertia constant is 4 seconds. Each transmission line has a per-unit impedance (with 100 MVA base) of j0.06. A fault occurs at time = 0 one-third of the way down one of the lines, closer to the generator than the infinite bus.

## Slide 11: Example 11.5

## Slide 12: Transient Stability Example, Cont'd

## Slide 13: Two-Axis Synchronous Machine Model
Classical model is appropriate only for the most basic studies; no longer widely used in practice
More realistic models are required to couple in other devices such as exciters and governors
A more realistic synchronous machine model requires that the machine be expressed in a reference frame that rotates at rotor speed
Standard approach is d-q reference frame, in which the major (direct or d-axis) is aligned with the rotor poles and the quadrature (q-axis) leads the direct axis by 90

## Slide 14: Synchronous Machine Modeling
3 bal. windings (a,b,c) – stator
Field winding (fd) on rotor
Damper in “d” axis
(1d) on rotor
2 dampers in “q” axis
(1q, 2q) on rotor
Damper windings are added to damp out oscillations

## Slide 15: Two Main Types of Synchronous Machines
Round Rotor
  Air-gap is constant, used with higher speed machines
Salient Rotor (often called Salient Pole)
  Air-gap varies circumferentially
  Used with many pole, slower machines such as hydro
  Narrowest part of gap in the d-axis and the widest along the q-axis

## Slide 16: DQ Reference Frame
Machine voltage and current are “transformed” into the d-q reference frame using the rotor angle, 
  Terminal voltage in network (power flow) reference frame are VT = Vr - Vi

## Slide 17: Two-Axis Model Equations
Numerous models exist for synchronous machines. The following is a relatively simple model that represents the field winding and one damper winding; it also includes the generator swing eq.

## Slide 18: Generator Exciters and Governors
The two-axis synchronous model takes as an input the field voltage and the mechanical power. The next section discusses how these values are controlled

## Slide 19: Generator Exciters
The purpose of the exciter is to maintain the generator terminal voltage (or other close by voltage) at a specified value.
  Input is the sensed voltage
  Output is the field voltage to the machine, Efd
Physically several technologies are used.
  Older generators used dc machines with brushes transferring the power
  With the newer brushless (or static) exciters power is obtained from an “inverted” synchronous generator whose field voltage is on the stator and armature windings are on rotor; output is rectified to create dc.

## Slide 20: ABB UNICITER Example
Image source: www02.abb.com, Brushless Excitation Systems Upgrade,

## Slide 21: Exciter Block Diagrams
Block diagrams are used to set up the transient stability models. The common IEEE Type 1 exciter is shown below (neglecting saturation); this is a dc type exciter. Initial state values are determined by knowing Efd and the terminal voltage Vt.

## Slide 22: Exciter Block Diagram Example
Consider the Example 11.10 case, with an IEEE T1 exciter with Tr = 0, Ka = 100, Ta = 0.05, Vrmax = 5, Vrmin = -5, Ke = 1, Te = 0.26, Kf = 0.01 and Tf = 1.0. Determine the initial states. Initial value of Efd = 2.9135 and Vt = 1.0946

## Slide 23: PowerWorld Example 12.1 Solution

## Slide 24: Generator Governors
The other key generator control system is the governor, which changes the mechanical power into the generator to maintain a desired speed and hence frequency.
Historically centrifugal “flyball” governors have been used to regulate the speed of devices such as steam engines
The centrifugal force varies with speed, opening or closing the throttle valve
Photo source: en.wikipedia.org/wiki/Centrifugal_governor

## Slide 25: Isochronous Governors
Ideally we would like the governor to maintain the frequency at a constant value of 60 Hz (in North America)
This can be accomplished using an isochronous governor.
  A flyball governor is not an isochronous governor since the control action is proportional to the speed error
  An isochronous governor requires an integration of the speed error
Isochronous governors are used on stand alone generators but cannot be used on interconnected generators because of “hunting”

## Slide 26: Generator “Hunting”
Control system “hunting” is oscillation around an equilibrium point
Trying to interconnect multiple isochronous generators will cause hunting because the frequency setpoints of the two generators are never exactly equal
  One will be accumulating a frequency error trying to speed up the system, whereas the other will be trying to slow it down
  The generators will not share the power load proportionally.

## Slide 27: Droop Control
The solution is to use what is known as droop control, in which the desired set point frequency is dependent upon the generator’s output
R is known as the regulation constant or droop; a typical value is 4 or 5%.

## Slide 28: Governor Block Diagrams
The block diagram for a simple stream unit, the TGOV1 model, is shown below. The T1 block models the governor delays, whereas the second block models the turbine response.

## Slide 29: Example 12.4 System Response

## Slide 30: Restoring Frequency to 60 Hz
In an interconnected power system the governors do not automatically restore the frequency to 60 Hz
Rather this is done via the ACE (area control area calculation). Previously we defined ACE as the difference between the actual real power exports from an area and the scheduled exports. But it has an additional term ACE =
b is the balancing authority frequency bias in MW/0.1 Hz with a negative sign. It is about 0.8% of peak load/generation

## Slide 31: 2600 MW Loss Frequency Recovery
Frequency recovers in about ten minutes