## Slide 1: ECEN 615, Fall 2023 Methods of Electric Power System Analysis
Prof. Adam Birchfield
Dept. of Electrical and Computer Engineering
Texas A&M University
abirchfield@tamu.edu
Class 10: Large Power System Operations and Control, Part 1

## Slide 2: Dispatch
Statement 1. All else being equal, the lowest-cost generators are dispatched to meet the load.
The major variable cost in power systems is associated with generation.
Cost to generate a MWh can vary widely.
For some types of units (such as hydro and nuclear) it is difficult to quantify.
For thermal units it is much easier, as we will discuss.
Economic dispatch (ED) determines the least cost dispatch of generation for an area.
For a lossless system, the ED occurs when all the generators have equal marginal costs. IC1(PG,1) = IC2(PG,2) = … = ICm(PG,m)

## Slide 3: Transmission Limits
Statement 2. Transmission lines and transformers have power flow limits, and good operations means transmission lines and transformers must stay within their limits.
As we discussed when studying transmission lines, these limits occur from several factors, such as thermal constraints, angle limits, and stability
For transformers the limits are thermal and saturation based
North American Electric Reliability Corporation (NERC) now has legal authority to enforce reliability standards (and there are now lots of them). See www.nerc.com/pa/stand/pages/reliabilitystandards.aspx

## Slide 4: Transmission Limits
Statement 3. The only direct way to control the power through a line is by opening and closing its associated circuit breakers.
This will cause the line flow to almost instantaneously change.
There is no other way to directly control line flow – i.e. no "valves" as in piping.
Note that opening a line because it is overloaded is usually a bad idea, because the flows will have to redistributed to other lines, potentially causing a cascade!

## Slide 5: Modeling Consideration – Change is Not Really Instantaneous!
The change isn’t really instantaneous because of propagation delays, which are near the speed of light; there also wave reflection issues
  This is covered in chapters 5 and 13
Red is the vs end, green the v2 end

## Slide 6: Transmission Limits
Statement 4. Indirect transmission flow control can be done by changing generator outputs.
Example of an overloaded transmission line. To fix this, indirectly change the flow by adjusting generator outputs.

## Slide 7: Transmission Limits
Statement 5. Real power flow is closely tied with the phase angle of the bus voltage, so phase shifters can be used to help control real power flows indirectly.
Go back to the derivation of the Fast-Decoupled Power Flow and see from the equations why and are so closely related.

## Slide 8: Volt-Var Control
Statement 6. Buses have a minimum and maximum voltage magnitude limit that must be maintained in good operations.
These are also covered by NERC standards. Typical limits would be 0.95 for a minimum limit and 1.08 for a maximum limit

## Slide 9: Volt-Var Control
Statement 7. Reactive power flow is closely tied with the voltage magnitude of buses, so volts and vars are often coordinated together.
Again, go back to the derivation of the Fast-Decoupled Power Flow to see from the equations why and are so closely related.
2.

## Slide 10: Volt-Var Control
Statement 8. Generator voltage magnitudes are scheduled, with generators changing their reactive power output to control their voltage.
Statement 9. Some transformers have variable tap ratios that can be used to control voltage.

## Slide 11: Volt-Var Control
Statement 10. Reactive power resources, such a shunt capacitors, static VAR compensators, and synchronous condensers, are primarily used as voltage control devices.
Reactive power controllers include switched shunts, static var compensators (SVCs), LTC transformers, sometimes generator voltage setpoints
Goal is to maintain adequate system voltages and reduce losses
Reactive power control is much less linear than real power control; this is partially due to the much higher reactive power losses because for high voltage transmission lines X is usually much larger than R
  Losses are very nonlinear
Vars do not travel far

## Slide 12: Example: ERCOT Competitive Renewable Energy Zones (CREZ) Study
In 2005 Texas Legislature ordered a grid study in order to accommodate more renewable generation in West Texas; reactive compensation was a key aspect
Source: www.ercot.com/content/news/presentations/2010/CREZ%20Reactive%20Power%20Compensation%20Study.pdf
Starting System Topology
Shunt Additions (< 0=caps)
12

## Slide 13: Volt-Var Control
Statement 11. Under-voltage is typically a problem in heavily loaded systems, needing more capacitor banks, while over-voltage can be a problem in lightly-loaded systems, needing more reactor banks.
The pi model when current is low will produce a lot of reactive power
The pi model when current is high will consume a lot of reactive power
Recall, the surge impedance loading (SIL) is on the boundary

## Slide 14: Power System Sensitivities
Statement 12. Sensitivities can be helpful to explain how different power values are related to each other, to give insights into control.
The assumption is
that the change
in generation is
absorbed by the
slack bus
We’ll do a lot more with these later in the semester…

## Slide 15: Contingency Analysis
Statement 14. Power systems are designed to be operated with N-1 security, that is, they would stay within limits after losing any single generator, line, or transformer.
Contingency analysis provides an automatic way of looking at all the statistically likely contingencies. In this example the contingency set is all the single line/transformer outages

## Slide 16: Losses
Statement 15. Generators must supply the power not only of loads but also of losses incurred in delivering power to the loads.
Typical on the transmission system is 3-5%, but a lot varies with the distance traveled and voltage levels used.

## Slide 17: Multi-Area Operation
Statement 16. Transmission interconnects are divided into large areas that monitor the total load, generation, losses, and interchange with other areas.

## Slide 18: Contiguous US Balancing Authority Areas
Image Source: www.eia.gov/todayinenergy/detail.php?id=27152

## Slide 19: Multi-Area Operation
Statement 17. Each area’s interchange must balance: Generation – Load – Losses = Exports – Imports.
Individual utilities only own and operate a small portion of the system, which is referred to an operating area (or an area).
Transmission lines that join two areas are known as tie-lines.
The net power out of an area is the sum of the flow on its tie-lines.
The flow out of an area is equal to total gen - total load - total losses = tie-flow
Trend is towards larger balancing authority areas
  ERCOT combined all their balancing authority areas in 2001

## Slide 20: Multi-Area Operation
Statement 18. An area schedules imports and exports with other areas, resulting in scheduled transactions requiring power transfers between the areas.
Scheduled 100 MW Transaction from Home Area to Other Area
Net tie-line
flow is now
100 MW

## Slide 21: Multi-Area Operation
Statement 19. Area control error (ACE) measures the difference between scheduled and actual net exports for an area.
Power transactions are contracts between areas to do power transactions.
Contracts can be for any amount of time at any price for any amount of power.
Scheduled power transactions are implemented by modifying the area ACE: ACE = Pactual,tie-flow - Psched

## Slide 22: Area Control Error (ACE)
The area control error is the difference between the actual flow out of an area, and the scheduled flow.
  There is also a frequency dependent component that we’ll address in Chapter 12
Ideally the ACE should always be zero.
Because the load is constantly changing, each utility must constantly change its generation to “chase” the ACE.

## Slide 23: MISO Real-Time ACE (US Members)
https://www.misoenergy.org/MARKETSOPERATIONS/REALTIMEMARKETDATA/Pages/ACEChart.aspx
Previously many MISO utilities did their own ACE calculations; now they are part of MISO, which does one for the region

## Slide 24: MISO Real-Time ACE Example
MISO's real-time ACE is available online (along with lots of other data)
https://www.misoenergy.org/MARKETSOPERATIONS/REALTIMEMARKETDATA/Pages/ACEChart.aspx

## Slide 25: Multi-Area Operation
Statement 20. Areas have an automatic generator control (AGC) system that sends signals to generators to change their MW outputs to help control the ACE and make sure load and generation balance with scheduled interchanges.
Most utilities use automatic generation control (AGC) to automatically change their generation to keep their ACE close to zero
Usually the utility control center calculates ACE based upon tie-line flows; then the AGC module sends control signals out to the generators every couple seconds.

## Slide 26: Three Bus Case with Manual ACE Control
Generation is manually
changed to match
change in load, keep ACE close to zero

## Slide 27: Three Bus Case with AGC
Generation real power is now being automatically controlled
Ripple is due to the deadband, used to prevent excessive change in the generation

## Slide 28: Multi-Area Operation
Statement 21. Transactions within areas and between areas will not exclusively follow the direct paths and may sometimes create loop flows through non-participating areas.

## Slide 29: Generator Dispatch and Electricity Pricing
Statement 22. The actual generator dispatch is by economics, but it is subject to constraints associated with transmission system, including contingency constraints.
Dispatch is no longer optimal due to need to keep line
from bus 2 to bus 3 from overloading

## Slide 30: Security Constrained Economic Dispatch
Transmission constraints often limit system economics.
Such limits required a constrained dispatch in order to maintain system security.
In three bus case the generation at bus 3 must be constrained to avoid overloading the line from bus 2 to bus 3.

## Slide 31: Generator Dispatch and Electricity Pricing
Statement 23. Electricity is priced locationally through locational marginal prices (LMPs).
Cost to supply electricity to bus is called the locational marginal price (LMP)
Presently some electric markets post LMPs on the web
In an ideal electricity market with no transmission limitations the LMPs are equal
Transmission constraints can segment a market, resulting in differing LMP
Determination of LMPs requires the solution on an Optimal Power Flow (OPF)

## Slide 32: ERCOT LMPs 9/9/17 at 12:47 PM
http://www.ercot.com/content/cdr/contours/rtmLmpHg.html

## Slide 33: MISO LMPs 9/13/17 at 8:10 AM
https://www.misoenergy.org/LMPContourMap/MISO_All.html

## Slide 34: Generator Dispatch and Electricity Pricing
Statement 24. Flowgates are constraints in the dispatch under base or contingency conditions, restricting the allowed flow through one or more parallel transmission paths.
The real-time loading of the power grid is accessed via “flowgates”
A flowgate “flow” is the real power flow on one or more transmission element for either base case conditions or a single contingency
  contingent flows are determined using LODFs
Flowgates are used as proxies for other types of limits, such as voltage or stability limits
Flowgates could be calculated using a spreadsheet
A list of the MISO flowgates is given at http://www.oatioasis.com/woa/docs/MISO/MISOdocs/MISO-COORDINATED_FLOWGATES.pdf