## Slide 1: ECEN 615, Fall 2023 Methods of Electric Power System Analysis
Prof. Adam Birchfield
Dept. of Electrical and Computer Engineering
Texas A&M University
abirchfield@tamu.edu
Class 7: Power Flow Computational Techniques and Approximations, Part 1

## Slide 2: Generator Control

## Slide 3: Generator Volt/Reactive Control
Simplest situation is a single generator at a bus regulating its own terminal
  Either PV, modeled as a voltage magnitude constraint, or as a PQ with reactive power fixed at a limit value. If PQ the reactive power limits can vary with the generator MW output
Next simplest is multiple generators at a bus. Obviously they need to be regulating the bus to the same voltage magnitude
  From a power flow solution perspective, it is similar to a single generator, with limits being the total of the individual units
  Options for allocation of vars among generators; this can affect the transient stability results

## Slide 4: Generator Remote Bus Voltage Control
Next complication is generators at a single bus regulating a remote bus; usually this is the high side of their generator step-up (GSU) transformer
  When multiple generators regulate a single point their exciters need to have a dual input
  This can be implemented in the power flow for the generators at bus j regulating the voltage at bus k by changing the bus j voltage constraint equation to be (however, this does create a zero on the diagonal of the Jacobian)
  Helps with power system voltage stability

## Slide 5: Generator Remote Bus Voltage Control
The next complication is to have the generators at multiple buses doing coordinated voltage control
  Controlled bus may or may not be one of the terminal buses
There must be an a priori decision about how much reactive power is supplied by each bus; example allocations are a fixed percentage or placing all generators at the same place in their regulation range
Implemented by designating one bus as the master; this bus models the voltage constraint
All other buses are treated as PQ, with the equation including a percent of the total reactive power output of all the controlling bus generators

## Slide 6: Reactive Power Sharing Options
Different software packages use different approaches for allocating the reactive power; PowerWorld has several options.

## Slide 7: Generator Voltage Control
This example uses the case PSC_37Bus with a voltage contour. Try varying the voltage setpoint for the generator at PEAR69

## Slide 8: Reactive Power Sharing
In this example, case PSC_37Bus_Varsharing, the two generators at Elm345 are jointly controlling Elms138

## Slide 9: Remote and Coordinated Var Control Example
Here the generators at Elm and the one at Birch are jointly controlling the voltage at the Lemon bus.
Case is PSC_37Bus_Varsharing_MultipleBuses

## Slide 10: Discussion: Power Flow Computational Methods
What part of the power flow is the most computationally expensive?
Any ideas to speed this up?
How can we tell if the power flow is not converging?
Any ideas to make it converge better?
Can we approximate Newton-Raphson to still get a solution with faster computation?
Could we make an approximation that would guarantee a solution?

## Slide 11: Power Flow Optimal Multiplier
Classic reference on power flow optimal multiplier is S. Iwamoto, Y. Tamura, “A Load Flow Calculation Method for Ill-Conditioned Power Systems,” IEEE Trans. Power App. and Syst., April 1981
Another paper is J.E. Tate, T.J. Overbye, “A Comparison of the Optimal Multiplier in Power and Rectangular Coordinates,” IEEE Trans. Power Systems, Nov. 2005
Key idea is once NR method has selected a direction, we can analytically determine the distance to move in that direction to minimize the norm of the mismatch
  Goal is to help with stressed power systems

## Slide 12: Power Flow with Optimal Multiplier
Consider an n bus power system with f(x) = S where S is the vector of the constant real and reactive power load minus generation at all buses except the slack, x is the vector of the bus voltages in rectangular coordinates: Vi = ei + jfi, and f is the function of the power balance constraints

## Slide 13: Power Flow with Optimal Multiplier
With a standard NR approach, we would get
If we are close enough to the solution the iteration converges quickly, but if the system is heavily loaded it can diverge

## Slide 14: Power Flow with Optimal Multiplier
Optimal multiplier approach modifies the iteration as
Scalar m is chosen to minimize the norm of the mismatch F in direction x
Paper by Iwamoto, Y. Tamura from 1981 shows m can be computed analytically with little additional calculation when rectangular voltages are used

## Slide 15: Power Flow with Optimal Multiplier
Determination of m involves solving a cubic equation, which gives either three real solutions, or one real and two imaginary solutions
1989 PICA paper by Iba (“A Method for Finding a Pair of Multiple Load Flow Solutions in Bulk Power Systems”) showed that NR tends to converge along line joining the high and a low voltage solution
However, there are some model restrictions

## Slide 16: Sparse Matrix Methods
The crucial part of the computation of the power flow deals with the matrix algebra, building and factoring the Jacobian
The Jacobian is very sparse, that is, most entries are zero. For large systems, well over 99% of the entries are zero.
A lot of key computational techniques take advantage of this sparsity.
We'll be looking at these methods in more detail after the first exam.

## Slide 17: Quasi-Newton Power Flow Methods
First we consider some modified versions of the Newton power flow (NPF)
Since most of the computation in the NPF is associated with building and factoring the Jacobian matrix, J, the focus is on trying to reduce this computation
In a pure NPF J is build and factored each iteration
Over the years pretty much every variation of the NPF has been tried; here we just touch on the most common
Whether a method is effective can be application dependent
  For example, in contingency analysis we are usually just resolving a solved case with an often small perturbation

## Slide 18: Quasi-Newton Power Flow Methods
The simplest modification of the NPF results when J is kept constant for a number of iterations, say k iterations
  Sometimes known as the Dishonest Newton
The approach balances increased speed per iteration, with potentially more iterations to perform
There is also an increased possibility for divergence
Since the mismatch equations are not modified, if it converges it should converge to the same solution as the NPF
These methods are not commonly used, except in very short duration, sequential power flows with small mismatches

## Slide 19: Dishonest N-R Example
We pay a price
in increased
iterations, but
with decreased
computation
per iteration; that price is too high in this example

## Slide 20: NPF (Honest) Region of for Two Bus Example Convergence
Red region converges to the high voltage solution, while the yellow region converges to the low voltage solution
Maximum of 15 iterations

## Slide 21: Two Bus Dishonest ROC
In this case being honest pays! At least with respect to the region of convergence (ROC)

## Slide 22: Quasi-Newton Power Flow Methods
A second modification is to modify the step size in the direction given by the NPF
  This is one we’ve already considered with the optimal multiplier approach
The generalized approach is to solve what is known as the line search (i.e., a one-dimensional optimization) to determine 

## Slide 23: The Single Dimensional  (l)
0

## Slide 24: Line Search
We need a cost function, which is usually the Euclidean norm of the mismatch vector
The line search is a general optimization problem for which there are many potential solution approaches
  Determines a local optimum within some search boundaries
  Approaches depend on whether there is gradient information available
Aside from the optimal multiplier approach, which can be quite helpful with little additional computation, the convergence gain from determining the “optimal”  is usually more than offset by the line search computation