## Slide 1: ECEN 615, Fall 2023 Methods of Electric Power System Analysis
Prof. Adam Birchfield
Dept. of Electrical and Computer Engineering
Texas A&M University
abirchfield@tamu.edu
Class 9: Power Flow Computational Techniques and Approximations, Part 3

## Slide 2: Fast Decoupled Power Flow
By continuing with our Jacobian approximations we can actually obtain a reasonable approximation that is independent of the voltage magnitudes/angles.
This means the Jacobian need only be built/inverted once per power flow solution
This approach is known as the fast decoupled power flow (FDPF)

## Slide 3: Fast Decoupled Power Flow, cont.
FDPF uses the same mismatch equations as standard power flow (just scaled) so it should have same solution
The FDPF is widely used, though usually only when we only need an approximate solution
Key fast decoupled power flow reference is B. Stott, O. Alsac, “Fast Decoupled Load Flow,” IEEE Trans. Power App. and Syst., May 1974, pp. 859-869
Modified versions also exist, such as D. Jajicic and A. Bose, “A Modification to the Fast Decoupled Power Flow for Networks with High R/X Ratios, “IEEE Transactions on Power Sys., May 1988, pp. 743-746

## Slide 4: FDPF Approximations
To see the impact on the real power equations recall

## Slide 5: FDPF Approximations
With the approximations for the diagonal term we get
Hence the Jacobian for the real equations can be approximated as –B

## Slide 6: FDPF Approximations
For the reactive power equations we also scale by Vi
For the Jacobian off-diagonals we get

## Slide 7: FDPF Approximations
And for the reactive power Jacobian diagonal we get
As derived the real and reactive equations have a constant Jacobian equal to –B
  Usually modifications are made to omit from the real power matrix elements that affect reactive flow (like shunts) and from the reactive power matrix elements that affect real power flow, like phase shifters
  We’ll call the real power matrix B’ and the reactive B”

## Slide 8: FDPF Three Bus Example
Use the FDPF to solve the following three bus system

## Slide 9: FDPF Three Bus Example, cont’d

## Slide 10: FDPF Three Bus Example, cont’d

## Slide 11: FDPF Region of Convergence

## Slide 12: FDPF Cautions
The FDPF works well as long as the previous approximations hold for the entire system
With the movement towards modeling larger systems, with more of the lower voltage portions of the system represented (for which r/x ratios are higher) it is quite common for the FDPF to get stuck because small portions of the system are ill-behaved
The FDPF is sometimes used to provide an initial guess of the solution or for contingency analysis

## Slide 13: DC Power Flow
The “DC” power flow makes the most severe approximations:
  completely ignore reactive power, assume all the voltages are always 1.0 per unit, ignore line conductance
This makes the power flow a linear set of equations, which can be solved directly
The term dc power flow actually dates from the time of the old network analyzers (going back into the 1930’s)
Not to be confused with the inclusion of HVDC lines in the standard NPF
P sign convention is generation is positive

## Slide 14: DC Power Flow References
I don’t think a classic dc power flow paper exists; a nice formulation is given in our book Power Generation and Control book by Wood, Wollenberg and Sheble
The August 2009 paper in IEEE Transactions on Power Systems, “DC Power Flow Revisited” (by Stott, Jardim and Alsac) provides good coverage
T. J. Overbye, X. Cheng, and Y. Sun, “A comparison of the AC and DC power flow models for LMP Calculations,” in Proc. 37th Hawaii Int. Conf. System Sciences, 2004, compares the accuracy of the approach

## Slide 15: DC Power Flow Example
Example from Power System Analysis and Design, by Glover, Overbye, Sarma, 6th Edition

## Slide 16: DC Power Flow in PowerWorld
PowerWorld allows for easy switching between the dc and ac power flows (case Aggieland37)
To use the dc approach in PowerWorld select Tools, Solve, DC Power Flow
Notice there are no losses