## Slide 1: ECEN 615, Fall 2023 Methods of Electric Power System Analysis
Prof. Adam Birchfield
Dept. of Electrical and Computer Engineering
Texas A&M University
abirchfield@tamu.edu
Class 12: Sparse Linear Systems, Part 1

## Slide 2: Second Half of the Semester
Main Topics
Sparse Linear Systems
Sensitivities
State Estimation
Optimization Methods and Applications
Special Topics, as time permits
Equivalents
Voltage stability
August 14, 2003 blackout
Synthetic grids
Geomagnetic disturbances
Power system restoration

## Slide 3: Reading Assignments for next week, Oct 18
Four papers to look at
N. Sato, W.F. Tinney, “Techniques for Exploiting the Sparsity of the Network Admittance Matrix,” Power App. and Syst., pp 944-950, December 1963
F. L. Alvarado, “Computational complexity in power systems,” IEEE Transactions on Power Apparatus and Systems, May/June 1976. Mainly the abstract, tables and figures, conclusion.
http://www.siam.org/meetings/la09/talks/duff.pdf
https://ieeexplore.ieee.org/abstract/document/9622790

## Slide 4: Assignment 3
Assignment 3 is on the website
Due Oct 25th
Review dense linear algebra techniques
You may use any programming language of your choice
Need to code up the algorithms as discussed in notes

## Slide 5: Linear System Solution: Introduction
A problem that occurs in many is fields is the solution of linear systems where A is an matrix with elements , and x and b are n-vectors with elements and respectively
In power systems we are particularly interested in systems when is relatively large and A is sparse
  How large is large is changing
A matrix is sparse if a large percentage of its elements have zero values
Goal is to understand the computational issues (including complexity) associated with the solution of these systems

## Slide 6: Introduction, cont.
Sparse matrices arise in many areas, and can have domain specific structures
  Symmetric matrices
  Structurally symmetric matrices
  Tridiagnonal matrices
  Banded matrices
A good (and free) book on sparse matrices is available at www-users.cs.umn.edu/~saad/IterMethBook_2ndEd.pdf
ECEN 615 is focused on problems in the electric power domain; it is not a general sparse matrix course
  Much of the early sparse matrix work was done in power!

## Slide 7: Dense Linear Algebra You Should Know
(“Dense” means regular, full, non-sparse matrices)
Basic matrix arithmetic: addition, multiplication
Gaussian Elimination (to solve Ax = b)
  Solve a system of equations
Triangular decomposition (to solve Ax = b)
  LU Factorization (and LDU)
  Pivoting
  Forward/Backward Solving

## Slide 8: Gaussian Elimination
The best known and most widely used method for solving linear systems of algebraic equations is attributed to Gauss
Gaussian elimination avoids having to explicitly determine the inverse of A, which is O()
Gaussian elimination can be readily applied to sparse matrices
Gaussian elimination leverages the fact that scaling a linear equation does not change its solution, nor does adding one linear equation to another

## Slide 9: Gaussian Elimination, cont.
Gaussian elimination is the elementary procedure in which we use the first equation to eliminate the first variable from the last n-1 equations, then we use the new second equation to eliminate the second variable from the last n-2 equations, and so on
After performing n-1 such eliminations we end up with a triangular system which is easily solved in a backward direction

## Slide 10: Example 1
We need to solve for x in the system
The three elimination steps are given on the next slides; for simplicity, we have appended the r.h.s. vector to the matrix
First step is set the diagonal element of row 1 to 1 (i.e., normalize it)

## Slide 11: Example 1, cont.
Eliminate by subtracting row 1 from all the rows below it

## Slide 12: Example 1, cont.
Eliminate by subtracting row 2 from all the rows below it

## Slide 13: Example 1, cont.
Elimination of from row 3 and 4

## Slide 14: Example 1, cont.
Then, we solve for by “going backwards”, i.e., using back substitution:

## Slide 15: Triangular Decomposition
In this example, we have:
  triangularized the original matrix by Gaussian elimination using column elimination
  then, we used back substitution to solve the triangularized system
The following slides present a general scheme for triangular decomposition by Gaussian elimination
The assumption is that A is a nonsingular matrix (hence its inverse exists)
Gaussian elimination also requires the diagonals to be nonzero; this can be achieved through ordering
If b is zero then we have a trivial solution x = 0

## Slide 16: Triangular Decomposition
We form the matrix using A and b with
  and show the steps of the triangularization scheme

## Slide 17: Triangular Decomposition, Step 1
Step 1: normalize the first equation

## Slide 18: Triangular Decomposition, Step 2
Step 2: a) eliminate x1 from row 2:
Step 2: b) normalize the second equation

## Slide 19: Triangular Decomposition, Step 2
and we end up at the end of step 2 with

## Slide 20: Triangular Decomposition, Step 3
Step 3: a) eliminate x1 and x2 from row 3:
Step 3: b) normalize the third equation:

## Slide 21: Triangular Decomposition, Step 3
and we have the system at the end of step 3

## Slide 22: Triangular Decomposition, Step k
In general, we have for step k: a) eliminate from row k:
b) normalize the kth equation:

## Slide 23: Triangular Decomposition: Upper Triangular Matrix
and proceed in this manner until we obtain the upper triangular matrix (the nth derived system):

## Slide 24: Triangular Decomposition
Note that in the scheme presented, unlike in the first example, we triangularly decompose the system by eliminating row-wise rather than column-wise
  In successive rows we eliminate (reduce to 0) each element to the left of the diagonal rather than those below the diagonal
  Either could be used, but row-wise operations will work better for power system sparse matrices

## Slide 25: Solving for X
To compute x we perform back substitution

## Slide 26: Upper Triangular Matrix
The triangular decomposition scheme applied to the matrix A results in the upper triangular matrix U with the elements
The following theorem is important in the development of the sparse computational scheme

## Slide 27: LU Decomposition Theorem
Any nonsingular matrix A has the following factorization:
Where U could be the upper triangular matrix previously developed (with 1’s on its diagonals) and L is a lower triangular matrix defined by

## Slide 28: LU Decomposition Application
As a result of this theorem we can rewrite
Can also be set so U has non unity diagonals
Once A has been factored, we can solve for x by first solving for y, a process known as forward substitution, then solving for x in a process known as back substitution
In the previous example we can think of L as a record of the forward operations preformed on b.

## Slide 29: LDU Decomposition
In the previous case we required that the diagonals of U be unity, while there was no such restriction on the diagonals of L
An alternative decomposition is
where D is a diagonal matrix, and the lower triangular matrix is modified to require unity for the diagonals

## Slide 30: Symmetric Matrix Factorization
The LDU formulation is quite useful for the case of a symmetric matrix
Hence only the upper triangular elements and the diagonal elements need to be stored, reducing storage by almost a factor of 2

## Slide 31: Symmetric Matrix Factorization
There are also some computational benefits from factoring symmetric matrices. However, since symmetric matrices are not common in power applications, we will not consider them in-depth
However, topologically symmetric sparse matrices are quite common, so those will be our main focus

## Slide 32: Pivoting
An immediate problem that can occur with Gaussian elimination is the issue of zeros on the diagonal; for example
This problem can be solved by a process known as “pivoting,” which involves the interchange of either both rows and columns (full pivoting) or just the rows (partial pivoting)
  Partial pivoting is much easier to implement, and actually can be shown to work quite well

## Slide 33: Pivoting, cont.
In the previous example the (partial) pivot would just be to interchange the two rows obviously we need to keep track of the interchanged rows!
Partial pivoting can be helpful in improving numerical stability even when the diagonals are not zero
  When factoring row k interchange rows so the new diagonal is the largest element in column k for rows j >= k

## Slide 34: LU Algorithm Without Pivoting Processing by row
We will use the more common approach of having ones on the diagonals of L. Also in the common, diagonally dominant power system problems pivoting is not needed Below algorithm is in row form (useful with sparsity!)
For i := 2 to n Do Begin // This is the row being processed
For j := 1 to i-1 Do Begin // Rows subtracted from row i
A[i,j] = A[i,j]/A[j,j] // This is the scaling
For k := j+1 to n Do Begin // Go through each column in i
A[i,k] = A[i,k] - A[i,j]*A[j,k]
End;
End;
End;

## Slide 35: LU Example
Starting matrix
First row is unchanged; start with i=2
Result with i=2, j=1; done with row 2

## Slide 36: LU Example, cont.
Result with i=3, j=1;
Result with i=3, j=2; done with row 3; done!

## Slide 37: LU Example, cont.
Original matrix is used to hold L and U
With this approach the original A matrix has been replaced by the factored values!

## Slide 38: Forward Substitution
Forward substitution solves with values in b being overwritten (replaced by the y values) For i := 2 to n Do Begin // This is the row being processed
For j := 1 to i-1 Do Begin
b[i] = b[i] - A[i,j]*b[j] // This is just using the L matrix
End;
End;

## Slide 39: Forward Substitution Example

## Slide 40: Backward Substitution
Backward substitution solves (with values of y contained in the b vector as a result of the forward substitution)
For i := n to 1 Do Begin // This is the row being processed
For j := i+1 to n Do Begin
b[i] = b[i] - A[i,j]*b[j] // This is just using the U matrix
End;
b[i] = b[i]/A[i,i] // The A[i,i] values are <> 0 if it is nonsingular
End

## Slide 41: Backward Substitution Example

## Slide 42: Computational Complexity
Computational complexity indicates how the number of numerical operations scales with the size of the problem
Computational complexity is expressed using the “Big O” notation; assume a problem of size n
  Adding the number of elements in a vector is O(n)
  Adding two n by n full matrices is O(n2)
  Multiplying two n by n full matrices is O(n3)
  Inverting an n by n full matrix, or doing Gaussian elimination is O(n3)
  Solving the traveling salesman problem by brute-force search is O(n!)

## Slide 43: Computational Complexity
Knowing the computational complexity of a problem can help to determine whether it can be solved (at least using a particular method)
  Scaling factors do not affect the computation complexity
    an algorithm that takes /2 operations has the same computational complexity of one the takes /10 operations (though obviously the second one is faster!)
With O() factoring a full matrix becomes computationally intractable quickly!
  A 100 by 100 matrix takes a million operations (give or take)
  A 1000 by 1000 matrix takes a billion operations
  A 10,000 by 10,000 matrix takes a trillion operations!

## Slide 44: Sparse Systems
The material presented so far applies to any arbitrary linear system
The next step is to see what happens when we apply triangular factorization to a sparse matrix
For a sparse system, only nonzero elements need to be stored in the computer since no arithmetic operations are performed on the 0’s
The triangularization scheme is adapted to solve sparse systems in such a way as to preserve the sparsity as much as possible

## Slide 45: Sparse Matrix History
A nice overview of sparse matrix history is by Iain Duff at http://www.siam.org/meetings/la09/talks/duff.pdf
Sparse matrices developed simultaneously in several different disciplines in the early 1960’s with power systems definitely one of the key players (Bill Tinney from BPA)
Different disciplines claim credit since they didn’t necessarily know what was going on in the others

## Slide 46: Sparse Matrix History
In power systems a key N. Sato, W.F. Tinney, “Techniques for Exploiting the Sparsity of the Network Admittance Matrix,” Power App. and Syst., pp 944-950, December 1963
    In the paper they are proposing solving systems with up to 1000 buses (nodes) in 32K of memory!
    You’ll also note that in the discussion by El-Abiad, Watson, and Stagg they mention the creation of standard test systems with between 30 and 229 buses (this surely included the now famous 118 bus system)
    The BPA authors talk “power flow” and the discussors talk “load flow.”
Tinney and Walker present a much more detailed approach in their 1967 IEEE Proceedings paper titled “Direct Solutions of Sparse Network Equations by Optimally Order Triangular Factorization”

## Slide 47: Sparse Matrix Computational Order
The computational order of factoring a sparse matrix, or doing a forward/backward substitution depends on the matrix structure
  Full matrix is O()
  A diagonal matrix is O(n); that is, just invert each element
For power system problems the classic paper is F. L. Alvarado, “Computational complexity in power systems,” IEEE Transactions on Power Apparatus and Systems, May/June 1976
  O() for factoring, O() for forward/backward
  For a 100,000 by 100,000 matrix changes computation for factoring from 1 quadrillion to 10 million!

## Slide 48: Inverse of a Sparse Matrix
The inverse of a sparse matrix is NOT in general a sparse matrix
We never (or at least very, very, very seldom) explicitly invert a sparse matrix
  Individual columns of the inverse of a sparse matrix can be obtained by solving x = A-1b with b set to all zeros except for a single nonzero in the position of the desired column
  If a few desired elements of A-1 are desired (such as the diagonal values) they can usually be computed quite efficiently using sparse vector methods (a topic we’ll be considering soon)
We can’t invert a singular matrix (with sparse or not)

## Slide 49: Computer Architecture Impacts
With modern computers the processor speed is many times faster than the time it takes to access data in main memory
  Some instructions can be processed in parallel
Caches are used to provide quicker access to more commonly used data
  Caches are smaller than main memory
  Different cache levels are used with the quicker caches, like L1, have faster speeds but smaller sizes; L1 might be 64K, whereas the slower L2 might be 1M
Data structures can have a significant impact on sparse matrix computation

## Slide 50: ECEN 615 Sparsity Limitations
Sparse matrices arise in many areas, and can have domain specific structures
  Symmetric matrices
  Structurally symmetric matrices
  Tridiagnonal matrices
  Banded matrices
ECEN 615 is focused on problems that arise in the electric power; it is not a general sparse matrix course

## Slide 51: Full Matrix versus Sparse Matrix Storage
Full matrices are easily stored in arrays with just one variable needed to store each value since the value’s row and column are implicitly available from its matrix position
With sparse matrices two or three elements are needed to store each value
  The zero values are not explicitly stored
  The value itself, its row number and its column number
  Storage can be reduced by storing all the elements in a particular row or column together
Because large matrices are often quite sparse, the total storage is still substantially reduced

## Slide 52: Sparse Matrix Usage Can Determine the Optimal Storage
How a sparse matrix is used can determine the best storage scheme to use
  Row versus column access; does structure change
Is the matrix essentially used only once? That is, its structure and values are assumed new each time used
Is the matrix structure constant, with its values changed
  This would be common in the N-R power flow, in which the structure doesn’t change each iteration, but its values do
Is the matrix structure and values constant, with just the b vector in Ax=b changing
  Quite common in transient stability solutions

## Slide 53: Numerical Precision
Required numerical precision determines type of variables used to represent numbers
  Specified as number of bytes, and whether signed or not
For Integers
  One byte is either 0 to 255 or -128 to 127
  Two bytes is either smallint (-32,768 to 32,767) or word (0 to 65,536)
  Four bytes is either Integer (-2,147,483,648 to 2,147,483,647) or Cardinal (0 to 4,294,967,295)
    This is usually sufficient for power system row/column numbers
  Eight bytes (Int64) if four bytes is not enough

## Slide 54: Numerical Precision, cont.
For floating point values using choice is between four bytes (single precision) or eight bytes (double precision); extended precision has ten bytes
  Single precision allows for 6 to 7 significant digits
  Double precision allows for 15 to 17 significant digits
  Extended allows for about 18 significant digits
  More bytes requires more storage
  Computational impacts depend on the underlying device; on PCs there isn’t much impact; GPUs can be 3 to 8 times slower for double precision
For most power problems double precision is best

## Slide 55: General Sparse Matrix Storage
A general approach for storing a sparse matrix would be using three vectors, each dimensioned to number of elements
  AA: Stores the values, usually in power system analysis as double precision values (8 bytes)
  JR: Stores the row number; for power problems usually as an integer (4 bytes)
  JC: Stores the column number, again as an integer
If unsorted then both row and column are needed
New elements could easily be added, but costly to delete
Unordered approach doesn’t make for good computation since elements used next computationally aren’t necessarily nearby
Usually ordered, either by row or column

## Slide 56: Sparse Storage Example
Assume
Then
Note, this example is a symmetric matrix, but the technique is general

## Slide 57: Compressed Sparse Row Storage
If elements are ordered (as was case for previous example) storage can be further reduced by noting we do not need to continually store each row number
A common method for storing sparse matrices is known as the Compressed Sparse Row (CSR) format
  Values are stored row by row
  Has three vector arrays:
    AA: Stores the values as before
    JA: Stores the column index (done by JC in previous example)
    IA: Stores the pointer to the index of the beginning of each row

## Slide 58: CSR Format Example
Assume as before
Then

## Slide 59: CSR Comments
The CSR format reduces the storage requirements by taking advantage of needing only one element per row
The CSR format has good advantages for computation when using cache since (as we shall see) during matrix operations we are often sequentially going through the vectors
An alternative approach is Compressed Sparse Column (CSC), which identical, except storing the values by column
It is difficult to add values.
We’ll mostly use the linked list approach here, which makes matrix manipulation simpler

## Slide 60: Linked Lists: Classes and Objects
In explaining the linked list approach it is helpful to use the concepts from object oriented programming (OOP) of classes and objects
  Approach can also be used in non-OOP programming
OOP can be thought of as a collection of objects interacting with each other
Objects are instances of classes.
Classes define the object fields and actions (methods)
We’ll define a class called sparse matrix element, with fields of value, column and next; each sparse matrix element is then an object of this class

## Slide 61: Linked Lists
A linked list is just a group of objects that represent a sequence
  We’ll used linked lists to represent a row or column of a sparse matrix
Each linked list has a head pointer that points to the first object in the list
  For our sparse matrices the head pointer will be a vector of the rows or columns
Column a
Value a
Next a
Column b
Value b
Next b
Column c
Value c
Nil
Head

## Slide 62: Sparse Matrix Storage with Linked Lists by Rows
If we have an n by n matrix, setup a class called TSparseElement with fields column, value and next
Setup an n-dimensional head pointer vector that points to the first element in each row
Each nonzero corresponds to an object of class (type) TSparseElement
We do not need to store the row number since it is given by the object’s row
For power system sparse matrices, which have nonzero diagonals, we also have a header pointer vector that points to the diagonal objects

## Slide 63: Linked Lists, cont.
Linked lists can be singly linked, which means they just go in one direction (to the next element), or doubly linked, pointing to both the previous and next elements
  Mostly we’ll just need singularly linked lists
With linked lists it is quite easy to add new elements to the list. This can be done in sorted order just by going down the list until the desired point is reached, then changing the next pointer for the previous element to the new element, and for the new element to the next element (for a singly linked list)

## Slide 64: On Board Example
Draw the data structures for the matrix

## Slide 65: Example Pascal Code for Writing a Sparse Matrix
Procedure TSparMat.SMWriteMatlab(Var ft : Text; variableName : String; digits,rod : Integer; ignoreZero : Boolean; local_MinValue : Double);
Var j : Integer;
p1 : TMatEle;
Begin
For j := 1 to n Do Begin
p1 := Row(j).Head;
While p1 <> nil Do Begin
If (not IgnoreZero) or (abs(p1.value) > local_MinValue) Then Begin
If variableName <> '' Then Writeln(ft,variableName+'(',(j),',',(p1.col),')=',p1.value:digits:rod,';')
Else Writeln(ft,j:5,' ',p1.col:5,' ',p1.value:digits:rod);
End;
p1 := p1.next;
End;
End;
End;

## Slide 66: Sparse Working Row
Before showing a sparse LU factorization it is useful to introduce the concept of a working row full vector
This is useful because sometimes we need direct access to a particular value in a row
The working row approach is to define a vector of dimension n and set all the values to zero
We can then load a sparse row into the vector, with computation equal to the number of elements in the row
We can then unload the sparse row from the vector by storing the new values in the linked list, and resetting the vector values we changed to zero

## Slide 67: Loading the Sparse Working Row
Procedure TSparMat.LoadSWRbyCol(rowJ : Integer; var SWR : PDVectorList);
Var p1 : TMatEle;
Begin
p1 := rowHead[rowJ];
While p1 <> nil Do Begin
SWR[p1.col] := p1.value;
p1 := p1.next;
End;
End;

## Slide 68: Unloading the Sparse Working Row
Procedure TSParMat.UnLoadSWRbyCol(rowJ : Integer; var SWR : PDVectorList);
Var p1 : TMatEle;
Begin
p1 := rowHead[rowJ];
While p1 <> nil Do Begin
p1.value := SWR[p1.col];
SWR[p1.col] := 0;
p1 := p1.next;
End;
End;
Note, there is no need to explicitly zero out all the elements each iteration since 1) most are still zero and 2) doing so would make it O(n2). The above code efficiently zeros out just the values that have changed.