## Slide 1: ECEN 615, Fall 2023 Methods of Electric Power System Analysis
Prof. Adam Birchfield
Dept. of Electrical and Computer Engineering
Texas A&M University
abirchfield@tamu.edu
Class 16: State Estimation, Part 1

## Slide 2: Second Half of the Semester
Main Topics
Sparse Linear Systems ✓
Sensitivities ✓
State Estimation
Optimization Methods and Applications
Special Topics, as time permits
Equivalents
Voltage stability
August 14, 2003 blackout
Synthetic grids
Geomagnetic disturbances
Power system restoration

## Slide 3: Intro to DC State Estimation
What is the load at bus 3?
Measurement | Value
 | 103.5 MW
 | 83.8 MW
 | 51.4 MW
 | 183.4 MW
 | 53.3 MW
 | 130.8 MW
Measurement | Value
 | 103.5 MW
 | 83.8 MW
 | 51.4 MW
 | 183.4 MW
 | 53.3 MW
 | 130.8 MW
Assume , ,

## Slide 4: Intro to DC State Estimation, cont.
, where are the two non-slack angles and
This is an overdetermined system! Note that A is not invertible. The method of least squares will help us get the best value of , to get the values close to the measurements. (We will find that it is )
This is the state estimation problem.

## Slide 5: Least Squares
So far we have considered the solution of Ax = b in which A is a square matrix; as long as A is nonsingular there is a single solution
  That is, we have the same number of equations (m) as unknowns (n)
Many problems are overdetermined in which there more equations than unknowns (m > n)
  Overdetermined systems are usually inconsistent, in which no value of x exactly solves all the equations
Underdetermined systems have more unknowns than equations (m < n); they never have a unique solution but might be consistent

## Slide 6: Method of Least Squares
The least squares method is a solution approach for determining an approximate solution for an overdetermined system
If the system is inconsistent, then not all of the equations can be exactly satisfied
The difference for each equation between its exact solution and the estimated solution is known as the error
Least squares seeks to minimize the sum of the squares of the errors
Weighted least squares allows differ weights for the equations

## Slide 7: Least Squares Solution History
The method of least squares developed from trying to estimate actual values from a number of measurements
Several persons in the 1700's, starting with Roger Cotes in 1722, presented methods for trying to decrease model errors from using multiple measurements
Legendre presented a formal description of the method in 1805; evidently Gauss claimed he did it in 1795
Method is widely used in power systems, with state estimation the best known application, dating from Fred Schweppe's work in 1970

## Slide 8: Least Squares and Sparsity
In many contexts least squares is applied to problems that are not sparse. For example, using a number of measurements to optimally determine a few values
  Regression analysis is a common example, in which a line or other curve is fit to potentially many points)
  Each measurement impacts each model value
In the classic power system application of state estimation the system is sparse, with measurements only directly influencing a few states
  Power system analysis classes have tended to focus on solution methods aimed at sparse systems; we'll consider both sparse and nonsparse solution methods

## Slide 9: Least Squares Problem
Consider
or

## Slide 10: Least Squares Solution
We write (ai)T for the row i of A and ai is a column vector
Here, m ≥ n and the solution we are seeking is that which minimizes |Ax – b|p, where p denotes some norm
Since usually an overdetermined system has no exact solution, the best we can do is determine an x that minimizes the desired norm.

## Slide 11: Choice of p
We discuss the choice of p in terms of a specific example
Consider the equation Ax = b with
(hence three equations and one unknown)
We consider three possible choices for p:

## Slide 12: Choice of p
(i) p = 1
(ii) p = 2
(iii) p = 

## Slide 13: Least Squares Solution
We write (ai)T for the row i of A and ai is a column vector
Here, m ≥ n and the solution we are seeking is that which minimizes |Ax – b|p, where p denotes some norm
Since usually an overdetermined system has no exact solution, the best we can do is determine an x that minimizes the desired norm.

## Slide 14: The Least Squares Problem
In general, is not differentiable for p = 1 or p = ∞
The choice of p = 2 (Euclidean norm) has become well established given its least-squares fit interpretation
The problem is tractable for two major reasons
  First, the function is differentiable

## Slide 15: The Least Squares Problem, cont.
  Second, the Euclidean norm is preserved under orthogonal transformations:
  with Q an arbitrary orthogonal matrix; that is, Q satisfies

## Slide 16: The Least Squares Problem, cont.
We introduce next the basic underlying assumption: A is full rank, i.e., the columns of A constitute a set of linearly independent vectors
This assumption implies that the rank of A is n because n ≤ m since we are dealing with an overdetermined system
Fact: The least squares solution x* satisfies

## Slide 17: Proof of Fact
Since by definition the least squares solution x* minimizes at the optimum, the derivative of this function zero:

## Slide 18: Implications
This underlying assumption implies that
Therefore, the fact that ATA is positive definite (p.d.) follows from considering any x ≠ 0 and evaluating
which is the definition of a p.d. matrix
We use the shorthand ATA > 0 for ATA being a symmetric, positive definite matrix

## Slide 19: Implications
The underlying assumption that A is full rank and therefore ATA is p.d. implies that there exists a unique least squares solution
Note: we use the inverse in a conceptual, rather than a computational, sense
The below formulation is known as the normal equations, with the solution conceptually straightforward

## Slide 20: Example: Curve Fitting
Say we wish to fit five points to a polynomial curve of the form
This can be written as

## Slide 21: Example: Curve Fitting
Say the points are t =[0,1,2,3,4] and y = [0,2,4,5,4]. Then

## Slide 22: Implications
An important implication of positive definiteness is that we can factor ATA since ATA > 0
The expression ATA = GTG is called the Cholesky factorization of the symmetric positive definite matrix ATA

## Slide 23: A Least Squares Solution Algorithm
  Step 1: Compute the lower triangular part of ATA
  Step 2: Obtain the Cholesky Factorization
  Step 3: Compute
  Step 4: Solve for y using forward substitution in
  and for x using backward substitution in
Note, our standard LU factorization approach would work; we can just solve it twice as fast by taking advantage of it being a symmetric matrix

## Slide 24: Practical Considerations
The two key problems that arise in practice with the triangularization procedure are:
  First, while A maybe sparse, ATA is much less sparse and consequently requires more computing resources for the solution
    In particular, with ATA second neighbors are now connected! Large networks are still sparse, just not as sparse
  Second, ATA may actually be numerically less well-conditioned than A

## Slide 25: Loss of Sparsity Example
Assume the B matrix for a network is
Then BTB is
Second neighbors are now connected!

## Slide 26: Numerical Conditioning
To understand the point on numerical ill- conditioning, we need to introduce terminology
We define the norm of a matrix to be
This is the maximum singular value of B

## Slide 27: Numerical Conditioning Example
Say we have the matrix
What value of x with a norm of 1 that maximizes ?

## Slide 28: Numerical Conditioning
i.e., li is a root of the polynomial
In other words, the 2 norm of B is the square root of the largest eigenvalue of BTB
Keep in mind the eigenvalues of a p.d. matrix are
positive

## Slide 29: Numerical Conditioning
The conditioning number of a matrix B is defined as
A well–conditioned matrix has a small value of
, close to 1; the larger the value of , the more pronounced is the ill-conditioning

## Slide 30: Power System State Estimation
Overall goal is to come up with a power flow model for the present "state" of the power system based on the actual system measurements
SE assumes the topology and parameters of the transmission network are mostly known
Measurements come from SCADA, and increasingly, from PMUs

## Slide 31: Power System State Estimation
Problem can be formulated in a nonlinear, weighted least squares form as where J(x) is the scalar cost function, x are the state variables (primarily bus voltage magnitudes and angles), zi are the m measurements, f(x) relates the states to the measurements and is the assumed standard deviation for each measurement

## Slide 32: Assumed Error
Hence the goal is to decrease the error between the measurements and the assumed model states x
The term weighs the various measurements, recognizing that they can have vastly different assumed errors
Measurement error is assumed Gaussian (whether it is or not is another question); outliers (bad measurements) are often removed

## Slide 33: State Estimation for Linear Functions
First we’ll consider the linear problem. That is where
Let R be defined as the diagonal matrix of the variances (square of the standard deviations) for each of the measurements

## Slide 34: State Estimation for Linear Functions
We then differentiate J(x) w.r.t. x to determine the value of x that minimizes this function

## Slide 35: Simple DC System Example
Say we have a two bus power system that we are solving using the dc approximation. Say the line’s per unit reactance is j0.1. Say we have power measurements at both ends of the line. For simplicity assume R=I. We would then like to estimate the bus angles. Then
We have a problem since HTH is singular. This is because of lack of an angle reference.

## Slide 36: Simple DC System Example, cont.
Say we directly measure q1 (with a PMU) to be zero; set this as the third measurement. Then
Note that the angles are in radians

## Slide 37: Nonlinear Formulation
A regular ac power system is nonlinear, so we need to use an iterative solution approach. This is similar to the Newton power flow. Here assume m measurements and n state variables (usually bus voltage magnitudes and angles) Then the Jacobian is the H matrix

## Slide 38: Measurement Example
Assume we measure the real and reactive power flowing into one end of a transmission line; then the zi-fi(x) functions for these two are
  Two measurements for four unknowns
Other measurements, such as the flow at the other end, and voltage magnitudes, add redundancy

## Slide 39: SE Iterative Solution Algorithm
We then make an initial guess of x, x(0) and iterate, calculating Dx each iteration
This is exactly the least squares form developed earlier with HTR-1H an n by n matrix. This could be solved with Gaussian elimination, but this isn't preferred because the problem is often ill-conditioned
Keep in mind that H is no longer constant, but varies as x changes. often ill-conditioned

## Slide 40: Nonlinear SE Solution Algorithm, Book Figure 9.11

## Slide 41: Example: Two Bus Case
Assume a two bus case with a generator supplying a load through a single line with x=0.1 pu. Assume measurements of the p/q flow on both ends of the line (into line positive), and the voltage magnitude at both the generator and the load end. So B12 = B21=10.0
We need to assume a reference angle unless we directly measuring phase

## Slide 42: Example: Two Bus Case
Let
We assume an angle reference of q1=0

## Slide 43: Example: Two Bus Case
With a flat start guess we get

## Slide 44: Example: Two Bus Case

## Slide 45: Assumed SE Measurement Accuracy
The assumed measurement standard deviations can have a significant impact on the resultant solution, or even whether the SE converges
The assumption is a Gaussian (normal) distribution of the error with no bias

## Slide 46: Exercise
Use Matlab to find the Least Squares solution to the DC state estimation problem on the handout (slides 2-3)
  Assume R=I
  Don’t forget to put P in per-unit!