## Slide 1: ECEN 615, Fall 2023 Methods of Electric Power System Analysis
Prof. Adam Birchfield
Dept. of Electrical and Computer Engineering
Texas A&M University
abirchfield@tamu.edu
Class 18: Power System Optimization, Part 1

## Slide 2: Assignment 5
Assignment 5 has to do with mixed-integer optimization using Python or Matlab with Gurobi (or another optimization platform)
You’ll be solving a unit commitment problem, which we’ll discuss in class next time.
Instructions from last time:
  Read through the assignment instructions
  Install and license Gurobi according to the instructions
  Set it up for Matlab or Python according to the instructions
  Run the example Matlab or Python case I provided you
  Bring your laptop to class
Get the example test problem to run in either Matlab or Python
Due date: November 20th, 2023 at 4pm

## Slide 3: Optimization
Parts of an optimization (or mathematical programming) problem
  Variables
  Objective – function we are trying to minimize (or maximize)
  Constraints – restrictions on the varaibles
    Equality
    Inequality
    Integer – must take integer values
Types of optimization problems
  Unconstrained vs Constrained
  Linear vs Nonlinear
  Continuous vs Integer vs Binary
  Mixed-integer linear, mixed-integer nonlinear
  Feasible solution – satisfies the constraints, regardless of objective
  Optimal solution – satisfies the constraints with the lowest possible objective
  Infeasible problem – no feasible solution exists

## Slide 4: Example Linear Continuous Problem
Assume that you operate a lumber mill which makes both construction-grade and finish-grade boards from the logs it receives. Suppose it takes 2 hours to rough-saw and 3 hours to plane each 1000 board feet of construction-grade boards. Finish-grade boards take 2 hours to rough-saw and 5 hours to plane for each 1000 board feet. Assume that the saw is available 8 hours per day, while the plane is available 15 hours per day. If the profit per 1000 board feet is $100 for construction-grade and $120 for finish-grade, how many board feet of each should you make per day to maximize your profit?
Notice that all of the equations are linear, all variables are continuous; we are seeking to determine the values of x1 and x2

## Slide 5: Example Mixed-Integer Linear Program
You want to optimize the 4 machines A-D in your chocolate factory for a six-day work week.
  Each machine needs at least two days off for maintenance.
  Each machine can only a maximum of 15 tons on any one day.
  You need to produce 11.3 tons of chocolate on Monday, 14.7 tons on Tuesday, 17.1 tons on Wednesday, 48.0 tons on Thursday, 19.6 tons on Friday, and 6.4 tons on Saturday.
  You want to minimize the total operating cost.
  Machine A costs $100 per ton.
  Machine B costs $200 per ton.
  Machine C costs $1000 per day.
  Machine D costs $2000 as a flat cost.
  How can you meet the chocolate production needs with a minimum cost?
Notice all the equations will be linear, but we have integer (binary) variables for whether the machines are on or off.

## Slide 6: Example Mixed-Integer Linear Program, Solution
For this problem, there are 4 machines by 6 days, or 24 binary variables for whether the machine is run on that day . There are also 24 real variables for the amount of chocolate produced by machine on day . Constraints:
Sum of for one machine should be <= 4
Each should be (Cannot produce negative chocolate)
Each should be
Sum of for each day should be equal to specified value.
The objective value is , where each of these variables is the sum over all the days.
The solution is $7410, with the variables printed in the output from the example Python and Matlab files. There are other examples that come with the Gurobi installation, as well as other documentation resources to get familiar with the Gurobi commands.

## Slide 7: Exercise
For the previous MIP, with code given
  How does the solution change if you have to produce one more ton on Saturday?
  How about on Tuesday?
  In the solution, which machine is used the most? The least?
  How do the different ways the four machines are priced affect the solution to the MIP?
(row=machine, column=day)
(row=machine, column=day)

## Slide 8: Power System Optimization Problems
Economic Dispatch (ED)
  Minimize generator cost
  Only constraints are total load and generator limits
  Does not consider transmission system
Optimal Power Flow (OPF)
  Combines economic dispatch with power flow
  Constraints include power flow balance equations, line flow limits, voltage limits
Security-constrained OPF (SCOPF)
  Must satisfy all OPF constraints in contingencies as well
Unit Commitment (UC)
  Determine which generators are on or off (committed) in a set of sequential time points
  Discussed in more detail in Chapter 4 of the book

## Slide 9: Solving Economic Dispatch
Economic dispatch is formulated as a constrained minimization
  The cost function is often total generation cost in an area
  Single equality constraint is the real power balance equation
Solved by setting up the Lagrangian (with PD the load and PL the losses, which are a function the generation)
A necessary condition for a minimum is that the gradient is zero. Without losses this occurs when all generators are dispatched at the same marginal cost (except when they hit a limit)

## Slide 10: Solving Economic Dispatch, Cont
If losses are neglected then there is a single marginal cost (lambda); if losses are included then each bus could have a different marginal cost

## Slide 11: Economic Dispatch Penalty Factors
The penalty factor
at the slack bus is
always unity!

## Slide 12: Optimal Power Flow (OPF)
Equality constraints
  bus real and reactive power balance
  generator voltage setpoints
  area MW interchange
Inequality constraints
  transmission line/transformer/interface flow limits
  generator MW limits
  generator reactive power capability curves
  bus voltage magnitudes
Available Controls
  generator MW outputs
  transformer taps and phase angles
  reactive power controls

## Slide 13: Two Example OPF Solution Methods
Non-linear approach using Newton’s method
  handles marginal losses well, but is relatively slow and has problems determining binding constraints
  Generation costs (and other costs) represented by quadratic or cubic functions
Linear Programming
  fast and efficient in determining binding constraints, but can have difficulty with marginal losses.
  used in PowerWorld Simulator
  generation costs (and other costs) represented by piecewise linear functions
Both can be implemented using an ac or dc power flow

## Slide 14: Two Example OPF Solution Methods
OPF (really SCOPF) is currently an area of active research, with ARPA-E having an SCOPF competition and recently awarding about $5 million for improved algorithms (see gocompetition.energy.gov)
A 2016 National Academies Press report, titled “Analytic Research Founds for the Next-Generation Electric Grid,” recommended improved AC OPF models
  It is available for free at www.nap.edu/catalog/21919/analytic-research-foundations-for-the-next-generation-electric-grid

## Slide 15: DC OPF and SCOPF
Solving a full ac OPF or SCOPF on a large system is difficult, so most electricity markets actually use the more approximate, but much simpler DCOPF, in which a dc power flow is used
PowerWorld includes this option in the Options, Power Flow Solution, DC Options
DC modeling can also be used for Unit Commitment (which we’ll be doing for Assignment 5)
https://www.ferc.gov/legal/staff-reports/2017/marginallosscalculations.pdf

## Slide 16: Unit Commitment
Goal is still to minimize generator costs
ED and OPF assume certain generators are online or offline
UC makes these decisions
  This introduces binary (integer) variables
  Solving for multiple time points in a row as load and renewable generation changes
Typical constraints
  Generator ramping rates
  Generator minimum up and minimum down times
  Must-run units, hydro unit coordination
  Area reserve requirements
Objective
  Generator cost c(p) as a function of output power
  Generator cost to start up
  Generator cost to shut down
  Generator fixed cost to operate if online

## Slide 17: Mixed-Integer Programming
A mixed-integer program (MIP) is an optimization problem of the form

## Slide 18: Mixed-Integer Programming
The advances in the algorithms have been substantial
Speedups from 2009 to 2015 were about a factor of 30!
Suppose you were given the following choices:
Solve a MIP with today’s solution technology on a 1991 machine
Solve a MIP with a 1991 solution on a machine from today?
The answer is to choose option 1, by a factor of approximately 300!
Notes are partially based on a presentation at Feb 2015 US National Academies Analytic Foundations of the Next Generation Grid by Robert Bixby from Gurobi Optimization titled “Advances in Mixed-Integer Programming and the Impact on Managing Electrical Power Grids”

## Slide 19: General Solver
OPF is currently an area of active research
Many formulations and solution methods exist…
  As do many tools for highly complex, large-scale computing!
While many options exist, some may work better for certain problems or with certain programs you already use
Consider experimenting with a new language/solver!
Gurobi and CPLEX are two well-known commercial optimization solvers/packages for linear programming (LP), quadratic programming (QP), quadratically constrained programming (QCP), and the mixed integer (MI) counterparts of LP/QP/QCP
Gurobi and CPLEX are accessible through object-oriented interfaces (C++, Java, Python, C), matrix-oriented interfaces (MATLAB) and other modeling languages (AMPL, GAMS)

## Slide 20: Assignment 5
A five-bus unit commitment problem with the following features
  Power flow is modeled with dc assumptions (4 bus theta variables)
  12 time points with varying load
  One wind generator with a varying maximum power
  7 total generating units
    Cost: start-up, shut-down, fixed, variable
    Minimum and maximum generation
  6 transmission lines have maximum flow limits
Solution will determine
  Status of generator at each of the 12 time points
  Generator output power p at each time point
  Line flow and bus angle at each time point
  Total cost of generation