## Slide 1: ECEN 460, Spring 2024 Power System Operation and Control
Prof. Adam Birchfield
Dept. of Electrical and Computer Engineering
Texas A&M University
abirchfield@tamu.edu
Class 1: Three-Phase AC Power Calculations

## Slide 2: Texas A&M is a Leader in Power and Energy Research
15 Faculty members in various expertise areas of power systems, power electronics, and electric machines
Graduate school is a great way to learn more in-depth topics and contribute to research projects (M.S. or Ph.D.)
Undergraduate research opportunities may be available
Right: Smart grid control center facility at RELLIS
Left: End of semester research group lunch
Top: TPEC is our student-led IEEE technical conference every February.

## Slide 3: Welcome to ECEN 460!
Syllabus and other important information, including slides will be on the website: https://birchfield.engr.tamu.edu/460s24/
Canvas is used for lab reports and grades
Textbook: Power System Analysis and Design
Evaluation
  15% First Exam, Tentatively Mar 7
  15% Second Exam, Tentatively April 11
  25% Final, May 6
  20% Quizzes and project
  25% Lab – starts next week
If you need accommodation for a disability, please let me know as soon as you can

## Slide 4: Some Things to Think About – For Next Class
What is energy? What is power?
Why is the bulk of the energy we use transmitted at some point by electricity?
Why is it important to have very high voltages in power systems?
Why do large electric power systems exclusively use AC at 50 or 60 Hz?
Why are large electric power systems exclusively three-phase?
Why are power grids connected across continents? What are the advantages or disadvantages of connecting to neighbors?

## Slide 5: Motivation for this Class
Electrification has changed the world!
  In 2000 the US National Academy of Engineering (NAE) named Electrification (the vast networks of electricity that power the developed world) as the top engineering technology of the 20th century
  Beating automobiles, airplanes, water, space flight
Power systems are critical to our way of life, and the 21st century is full of new challenges
  Increased and varying electric load
  Need for affordable electricity around the world
  Sustainability and environmental responsibility
  Resilience to natural and man-made threats

## Slide 6: What this Class Will Cover
Review of three-phase AC power calculations (today)
Structure, history, and design of power systems
Generator and load modeling
Transmission line and transformer modeling
The power flow problem and solution methods
Economic power system operation
Dynamics and stability of power systems
Emerging topics

## Slide 7: First Assignment – Review Three-Phase AC Power Calculations
Main topics you need to know
  Complex number math – by hand and calculator
  Phasors – representing AC voltage and current
  Impedance – for AC circuit solving
  Complex power – including power factor, reactive power
  Three phase – wye/delta, line-to-line/line-to-neutral voltage, per-phase analysis
Today we’re going to review these
Homework #1 and #2 are practice problems on these topics
  Homework #1 due next Tuesday (Jan 23) and Homework #2 due Tuesday Jan 30
There are four videos on the website that can help as well
Take advantage of the textbook, and office hours (me and TAs)
We’re going to have quizzes most classes to review.

## Slide 8: Review of Phasors – Representing AC Voltage and Current
The goal of phasor analysis is to simplify the analysis of constant frequency ac systems
We represent ac voltage and current as complex numbers
Euler’s Identity:
Phasor notation is developed by rewriting using Euler’s identity
(Note: |V| is the RMS voltage)
Root Mean Square (RMS) voltage of sinusoid

## Slide 9: Phasors, Cont.
The RMS, cosine-referenced voltage phasor is:
(Note: Some texts use boldface type for complex numbers; some use overbars)

## Slide 10: Impedance – For AC Circuit Solutions
(Note: Z is a complex number but not a phasor)
Device Time Analysis Phasor
Resistor
Inductor
Capacitor

## Slide 11: Impedance – RL Circuit Example
Given , calculate current time function.
Answer:

## Slide 12: Complex Power
Power
Power Factor Angle

## Slide 13: Complex Power, Cont’d
(Note: S is a complex number but not a phasor)
Real Power (W, kW, MW)
Reactive Power (var, kvar, Mvar)
Complex power (VA, kVA, MVA)
Power Factor (pf)
If current leads voltage then pf is leading
If current lags voltage then pf is lagging

## Slide 14: Complex Power, Cont’d
Relationships between real, reactive, and complex power
Example: A load draws 100 kW with a leading pf of 0.85. What are (power factor angle), and ?

## Slide 15: Conservation of Power
At every node (bus) in the system:
  Sum of real power into node must equal zero
  Sum of reactive power into node must equal zero
This is a direct consequence of Kirchhoff’s current law, which states that the total current into each node must equal zero.
  Conservation of power follows since S = VI*

## Slide 16: Power Consumption in Devices

## Slide 17: Example
First solve
basic circuit

## Slide 18: Example, Cont’d
Now add additional
reactive power load
and resolve

## Slide 19: Power System Notation
Power system components are usually shown as
“one-line diagrams.” Previous circuit redrawn
Arrows are
used to
show loads
Generators are
shown as circles
Transmission lines are shown as a single line

## Slide 20: Reactive Compensation
Key idea of reactive compensation is to supply reactive power locally. In the previous example this can be done by adding a 16 Mvar capacitor at the load
Reactive compensation decreased the line flow from 564 Amps to 400 Amps. This has advantages
  Lines losses, which are equal to I2 R decrease
  Lower current allows utility to use small wires, or alternatively, supply more load over the same wires
  Voltage drop on the line is less

## Slide 21: Reactive Compensation, Cont’d
Reactive compensation is used extensively by utilities
Capacitors can be used to “correct” a load’s power factor to an arbitrary value.
Distribution-level capacitor shown on right

## Slide 22: Power Factor Correction Example
Assume we have 100 kVA load with pf=0.8 lagging, and would like to correct the pf to 0.95 lagging
Similar example is given in video linked to website.

## Slide 23: Balanced Three-Phase () Systems
A balanced three-phase () system has
  three voltage sources with equal magnitude, but with an angle shift of 120
  equal loads on each phase
  equal impedance on the lines connecting the generators to the loads
Bulk power systems are almost exclusively 3
Single-phase is used primarily only in low voltage, low power settings, such as residential and some commercial
Advantages include transmitting more power for same amount of wire, and easier starting, better design, and constant torque for machines

## Slide 24: Balanced 3 -- No Neutral Current
+
–
–
+
–
+
Phase “a”
Phase “c”
Neutral “n”
Phase “b”

## Slide 25: Three-Phase Wye Connection
There are two ways to connect 3 systems
  Wye (Y)
  Delta ()
+
–
–
+
–
+
Phase “a”
Phase “c”
Neutral “n”
Phase “b”
Wye Connection Voltages

## Slide 26: Wye Connection Line Voltages
Van
Vcn
Vbn
Vab
Vca
Vbc
-Vbn
Line to line
voltages are
also balanced
(α = 0 in this case)

## Slide 27: Wye Connection, cont’d
Phase voltage: across wye-connected device
Phase current: through wye-connected device
Line voltage: voltage from one line to another
Line current: current through a line

## Slide 28: Delta Connection
Phase “a”
Phase “c”
Phase “b”
Ica
Ic
Iab
Ibc
Ia
Ib

## Slide 29: Three-Phase Example
Assume a -connected load is supplied from a 3 13.8 kV (L-L) source with Z = 10020
Phase “a”
Phase “c”
Phase “b”

## Slide 30: Three-Phase Example, cont’d

## Slide 31: Delta-Wye Transformation
To simplify analysis of balanced three-phase systems:
Delta connected loads can be replaced by wye-connected loads
Delta-connected sources can be replaced by wye-connected sources with

## Slide 32: Delta-Wye Transformation Proof

## Slide 33: Delta-Wye Transformation, cont’d

## Slide 34: Per Phase Analysis
Per phase analysis allows analysis of balanced three-phase systems with the same effort as for a single phase system
Balanced Three-Phase Theorem: For a balanced three-phase system with
  All loads and sources Y connected
  No mutual Inductance between phases
Then
  All neutrals are at the same potential
  All phases are completely decoupled
  All system values are the same sequence as sources. The sequence order we’ve been using (phase b lags phase a and phase c lags phase a) is known as “positive” sequence (negative and zero sequence systems are mostly covered in ECEN 459)

## Slide 35: Per Phase Analysis Procedure
To do per phase analysis
  Convert all  load/sources to equivalent Y’s
  Solve phase “a” independent of the other phases
  Total system power S = 3 Va Ia*
  If desired, phase “b” and “c” values can be determined by inspection (i.e., ±120° degree phase shifts)
  If necessary, go back to original circuit to determine line-line values or internal  values.

## Slide 36: Per Phase Example
Assume a 3, Y-connected generator with Van = 10 volts supplies a -connected load with Z = -j through a transmission line with impedance of j0.1 per phase. The load is also connected to a -connected generator with Va”b” = 10 through a second transmission line which also has an impedance of j0.1 per phase.
Find
1. The load voltage Va’b’
2. The total power supplied by each generator, SY and S

## Slide 37: Per Phase Example, cont’d

## Slide 38: Per Phase Example, cont’d

## Slide 39: Per Phase Example, cont’d

## Slide 40: Per Phase Example, cont’d

## Slide 41: Reminders
Review these topics
  Complex number math – by hand and calculator
  Phasors – representing AC voltage and current
  Impedance – for AC circuit solving
  Complex power – including power factor, reactive power
  Three phase – wye/delta, line-to-line/line-to-neutral voltage, per-phase analysis
Homework #1 and #2 are practice problems on these topics
  Homework #1 due next Tuesday (Jan 23) and Homework #2 due Tuesday Jan 30
  BUT please do them early to make sure you’ve got it
There are four videos on the website that can help as well
Take advantage of the textbook, and office hours (me and TAs)
We’re going to have quizzes most classes to review

## Slide 42: Aggie Core Values and Aggie Honor Code
Aggie Core Values
  Respect
  Excellence
  Leadership
  Loyalty
  Integrity
  Selfless Service
Aggie Honor Code: An Aggie does not lie, cheat, or steal, or tolerate those who do.
Reveille and I hope you have a great semester!