## Slide 1: ECEN 460, Spring 2024 Power System Operation and Control
Prof. Adam Birchfield
Dept. of Electrical and Computer Engineering
Texas A&M University
abirchfield@tamu.edu
Class 14: DC Power Flow Examples

## Slide 2: A DC Power Flow Example
Here were the impedances we found, in per-unit on the system base:
  Note: we are modeling the generator as the slack bus (no impedance) and the load as constant power 20 MW and 10 Mvar
Solve the system with the DC power flow

## Slide 3: A DC Power Flow Example, cont.
Make the y-bus matrix
2. Find the B matrix as the imaginary part of Y without the slack bus row/column
3. Find the P-vector of power injections and solve
Solution:

## Slide 4: Another Power Flow Example
For this four-bus power flow problem
  Make the Y-bus matrix
  Identify the bus type and known/unknown variables for each bus
  Write the P and Q equations for bus 4
  Write the last row () of the Jacobian matrix
Solve the dc power flow for this problem
  What is the approximate power flow on the line 1-2?
Bus 1
Bus 2
Bus 3
Bus 4
Bus 1: Generator with voltage setpoint of 1.00 pu
Bus 2: Generator with voltage setpoint of 1.02 pu and power setpoint of 75 MW
Bus 4: Load with 180 MW and 55 Mvar
Line 1-3: Z = j0.25
Line 1-2: Z = j0.05
Line 2-3: Z = j0.2
Line 3-4: Z = 0.04+j0.08

## Slide 5: Another Power Flow Example, Cont.
Y-bus matrix
Bus 1 is slack (unknown )
Bus 2 is PV (unknown /)
Buses 3&4 are PQ (unkn. )
In last row of Jacobian:

## Slide 6: Another Power Flow Example, dc part
B matrix – imaginary part of y-bus without slack row and column
P vector based on power leaving non-slack buses
Solve for theta (remember this is an approximation)
Get line flow based on dc assumptions
p.u. (or 22.5 MW)