## Slide 1: ECEN 460, Spring 2024 Power System Operation and Control
Prof. Adam Birchfield
Dept. of Electrical and Computer Engineering
Texas A&M University
abirchfield@tamu.edu
Class 6: Transformers, Part 2
Special guest lecturer TA Luke Lowery

## Slide 2: Homework 3 and 4
No homework on generators. Make sure you understand the lecture notes and labs 3 and 4 (starting next week).
Homework 3 on transformers: book problems 3.4, 3.23, due Feb. 8th.
Homework 4 on transmission lines: book regular problems 4.10, 4.11, 4.20, and 4.41, 5.14 (a,b), 5.38, and 5.41 (a,b), due Feb. 15th.

## Slide 3: Non-Ideal Transformer Example
Example: A single phase, 15 MVA, 35/13 kV transformer has the following test data:
open circuit: 14 amps, with 3 kW losses
short circuit: 6 kV, with 200 kW losses
Determine the model parameters.
n

## Slide 4: Transformer Example, Cont’d
From the short circuit test
From the open circuit test

## Slide 5: Relating to Lab 3
https://www.eeeguide.com/determination-of-the-synchronous-reactance/
The machine we will use in Lab 3
Unsaturated Synchronous Reactance Xu
Reactance before machine is saturated, follows AGL
Saturated Synchronous Reactance Xs
Reactance when machine in saturated state, calculate per saturated operating point

## Slide 6: Three Phase Per-Unit
Motivation
Proposal
A one-time value normalization that does this ‘voltage-level’ handling for us!
Actual Value Analysis
Solving this is hard, can’t it be easier?
50 MW
P=0.5
P=0.2
V = 1.08
P=0.3
V=1
115kV:69kV
20 MW
15kV
30 MW
13.8kV
13.8kV:115kV
13.8kV:69kV
13.8kV:69kV

## Slide 7: Three Phase Per-Unit
Goal Convert all grid values to Per-Unit
Stage 2 Convert to Per-Unit
Scaling actual observed values by their base converts the system to a unitless system that doesn’t care about ratings or voltage levels in analysis! (with ideal transformers)
Pros:
No Longer Have to Consider XFMRs
Easy calculations between HV/LV areas
Simplified View of System
Stage 1 Determine Bases
Power Base
  Reference Loading
Voltage Base
  Nominal Voltage
Impedance Base
  Impedance that Causes Reference Load
Current Base
  Current Value that Causes Reference Load

## Slide 8: Three Phase Per-Unit
Procedure is very similar to 1 phase except we use a 3 phase VA base, and use line to line voltage bases
Pick a VA base for the entire system
Pick a voltage base for each different voltage level, . Voltages are line to line.
Calculate the impedance base
Exactly the same impedance bases as with single phase!

## Slide 9: Three Phase Per-Unit
Step 1
Pick a VA base for the entire system
We always use 100 MVA for system-base
Step 2
Pick a voltage base for each Zone
Voltages are line-to-line
Step 3
Calculate the impedance base for Each Zone
Since we chose S & V, we must calculate Z to satisfy Ohm’s Law

## Slide 10: Three Phase Per-Unit , Cont'd
Step 4
Calculate the current base
CAREFUL!
Why in Current?
In this analysis, we care about line-to-neutral current, because this represents the ‘actual’ current flowing through the transmission line.
But since it is standard to use the line-to-line voltage, that means we are calculating a line-to-neutral value from a line-to-line value!
Load
Source

## Slide 11: Three Phase Per-Unit , Cont'd
Final Step
Convert All Values to Per-Unit
Lines, Transformers, Generators, Loads
From Steps 1-4
Transformers Where MVA != 100
or
MVA = 50
Z = 1%
13.8kV:138kV
Zone 1
Zone 2
LV
HV

## Slide 12: Three Phase Per-Unit
TA-DA!
Base Type | Formula
Power | 
Voltage | 
Impedance | 
Current | 
Base Type | Formula
Power | 
Voltage | 
Impedance | 
Current | 
Circuit Analysis
PU
XFMRs
Lines, Generators, Loads
Determine Bases per Zone
or
Actual

## Slide 13: Per Unit Change of MVA Base
Parameters for equipment are often given using power rating of equipment as the MVA base
To analyze a system all per unit data must be on a common power base

## Slide 14: Per Unit Change of Base Example
A 54 MVA transformer has a leakage reactance of 3.69%. What is the reactance on a 100 MVA base?

## Slide 15: Transformer Reactance
Transformer reactance is often specified as a percentage, say 10%. This is a per unit value (divide by 100) on the power base of the transformer.
Example: A 350 MVA, 230/20 kV transformer has leakage reactance of 10%. What is p.u. value on 100 MVA base? What is value in ohms (230 kV)?

## Slide 16: Three Phase Per-Unit Example
Solve for the current, load voltage and load power in the previous circuit, assuming a power base of 300 MVA, and line to line voltage bases of 13.8 kV,138 kV and 27.6 kV (square root of 3 larger than the 1f example voltages). Also assume the generator is Y-connected so its line to line voltage is 13.8 kV.
Convert to per unit
as before. Note the
system is exactly the
same!

## Slide 17: 3 Per-Unit Example, Cont'd
Again, analysis is exactly the same!

## Slide 18: 3 Per-Unit Example, Cont'd
Differences appear when we convert back to actual values

## Slide 19: 3 Per-Unit Example 2
Assume a load of 100+j50 MVA with of 69 kV is connected to a source through the below network:
What is the supply current and complex power?
Answer: I=467 amps, S = 103.3 + j76.0 MVA

## Slide 20: 3 Per-Unit Example 2
Assume a load of 100+j50 MVA with of 69 kV is connected to a source through the below network:
What is the supply current and complex power?
Answer: I=467 amps, S = 103.3 + j76.0 MVA
Zone 1
Zone 2
Convert to PU
Analysis in PU
Convert to Actual Values