## Slide 1: ECEN 460, Spring 2024 Power System Operation and Control
Prof. Adam Birchfield
Dept. of Electrical and Computer Engineering
Texas A&M University
abirchfield@tamu.edu
Class 9: Power Flow, Part 1

## Slide 2: Announcement
Homework #5: book problems 6.9, 6.12, 6.18, 6.25, 6.38, due 2/22/2024

## Slide 3: Recall, Transmission Line and Transformer Models
Transmission lines use the "pi" model
Transformer non-ideal model is simplified with the per-unit system (and neglecting shunt elements)
These devices reduce down to impedances

## Slide 4: Let's Start to Think About a Larger System
The most common power system analysis tool is the power flow – sometimes also called load flow
Power flow assumes system is in steady state
The goal is to solve the system state
  Bus complex voltages everywhere
  From these values we can get other values such as current and power flows

## Slide 5: Larger System – Network Equations

## Slide 6: Larger System – Network Equations, Cont.
KCL at bus 1
()
Similarly---

## Slide 7: Larger System – Network Equations as a Matrix

## Slide 8: Larger System – Network Equations as a Matrix
Put all the KCL equations together (using ) and we can make a matrix
This is the y-bus matrix

## Slide 9: Bus Network Admittance Matrix
Finding the bus network admittance matrix (y-bus) is the first step of the power flow
It shows the relationship between all the bus current injections I (from generation and load) and the bus voltages V

## Slide 10: Building the Y-Bus Matrix
Here are the steps for building the Y-bus matrix
  Start with an NxN matrix of all zeros (N is the number of buses)
  For any shunt elements, add to the corresponding diagonal elements of the Y-bus
  For branches between two buses,
    add to both diagonal elements of the Y-bus
    Subtract from both off-diagonal elements of the Y-bus
Example: if a transmission line from bus 12 to bus 17 has (per-unit) and then
  Add the shunt to matrix positions (12, 12) and (17, 17)
  Add the series to matrix positions (12, 12) and (17, 17)
  Subtract the series to matrix positions (12, 17) and (17, 12)
We add one network element at a time to the Y-bus matrix!

## Slide 11: Two-Bus Example
Here are the steps for building the Y-bus matrix
  Start with an NxN matrix of all zeros (N is the number of buses)
  For any shunt elements, add to the corresponding diagonal elements
  For branches,
    add to both diagonal elements
    Subtract from both off-diagonal elements
Try it on a two-bus system:

## Slide 12: Two-Bus Example
Here are the steps for building the Y-bus matrix
  Start with an NxN matrix of all zeros (N is the number of buses)
  For any shunt elements, add to the corresponding diagonal elements
  For branches,
    add to both diagonal elements
    Subtract from both off-diagonal elements
Try it on a two-bus system:

## Slide 13: Two-Bus Example, Continued
For the previous circuit, assume the voltages are and
What are the power injections of the source and load?

## Slide 14: Two-Bus Example, Continued
For the previous circuit, assume the voltages are and
What are the power injections of the source and load?

## Slide 15: Two-Bus Example, Continued
For the previous circuit, assume the current injections are and
What are the voltages and the power injections of the source and load?

## Slide 16: Two-Bus Example, Continued
For the previous circuit, assume the current injections are and
What are the voltages and the power injections of the source and load?

## Slide 17: Y-bus in PowerWorld
To see the Ybus in PowerWorld, select Case Information, Solution Details, Ybus
For large systems most of the Ybus elements are zero, giving what is known as a sparse matrix
Ybus for Lab 3 Three Bus System

## Slide 18: Modeling Generators and Loads for Power Flow
Generators
Engineering models depend upon application
Generators are usually synchronous machines
For generators we will use two different models:
  a short term model treating the generator as a constant voltage source behind a possibly time-varying reactance (used in Lab and earlier in class)
  a steady-state model, treating the generator as a constant power source operating at a fixed voltage; this model will be used for power flow and economic analysis
Loads
Ultimate goal is to supply loads with electricity at constant frequency and voltage
Electrical characteristics of individual loads matter, but usually they can only be estimated
  Actual loads are constantly changing, consisting of a large number of individual devices
  Only limited network observability of load characteristics
Aggregate models are typically used for analysis
Two common models
  Constant power: Si = Pi + jQi
  Constant impedance: Si = |V|2 / Zi

## Slide 19: The Power Flow Problem
What we know:
  Generator real power
  Generator voltage magnitude
  Load real and reactive power
What we don't know:
  Bus voltage angles
  Non-generator bus voltage magnitude
  Generator reactive power
  Current injections of generators or loads
Note that the problem is formulated with power values, not current, so we cannot use the Y-bus equations directly

## Slide 20: Linear vs. Non-Linear Systems
A function H is linear if
H(a1m1 + a2m2) = a1H(m1) + a2H(m2)
That is
1) the output is proportional to the input
2) the principle of superposition holds
Linear Example: y = H(x) = c x
y = c(x1+x2) = cx1 + c x2
Nonlinear Example: y = H(x) = c x2
y = c(x1+x2)2 ≠ (cx1)2 + (c x2)2

## Slide 21: Power Flow Problem is Non-Linear
The Y-Bus equations alone are very linear—can solve with superposition
Because of the way we model generators and loads with constant power characteristics, the problem becomes non-linear
Non-linear problems can be quite difficult to solve, and usually require an iterative approach.

## Slide 22: Something to Think About
How do we solve this DC circuit for different values of P?
P |  | 
0 W |  | 
1 W |  | 
2 W |  | 
4 W |  | 
5 W |  | 
6 W |  | 
10 W |  | 
P |  | 
0 W |  | 
1 W |  | 
2 W |  | 
4 W |  | 
5 W |  | 
6 W |  | 
10 W |  | 

## Slide 23: Possibly 0, 1, or Multiple Solutions to Non-Linear Problems
How do we solve this DC circuit for different values of P?
P | Load voltage and current | Alternative, low-voltage solution
0 W | 10 V, 0 A | 0 V, 2 A
1 W | 9.47 V, 0.11 A | 0.53 V, 1.89 A
2 W | 8.87 V, 0.23 A | 1.13 V, 1.77 A
4 W | 7.24 V, 0.55 A | 2.76 V, 1.45 A
5 W | 5 V, 1 A | 
6 W | No Solution | 
10 W | No Solution |