## Slide 1: ECEN 460, Spring 2024 Power System Operation and Control
Prof. Adam Birchfield
Dept. of Electrical and Computer Engineering
Texas A&M University
abirchfield@tamu.edu
Class 22: Additional Dynamics Topics

## Slide 2: The Generator Dynamic Equations We Will Use
Example power system problem with differential algebraic equations (DAEs) is the classical synchronous generator connected to an infinite bus.
The two differential variables are and ; in practice dynamic models can have many more.
Generator Parameters
is the machine inertia constant (in seconds)
is the synchronous frequency (260)
is the mechanical torque (power being supplied by the prime mover)
is the generator internal voltage, as controlled by the excitation system
is the generator transient impedance
damping constant of the generator
Infinite Bus / System
The infinite bus is defined by a Thevenin equivalent with voltage
And reactance
These are the harder variables to get.

## Slide 3: Control of Generation Overview
Goal is to maintain constant frequency with changing load
If there is just a single generator, such with an emergency generator or isolated system, then an isochronous governor is used
  Integrates frequency error to insure frequency goes back to the desired value
  Cannot be used with interconnected systems because of "hunting"
Image source: Wood/Wollenberg, 2nd edition

## Slide 4: Isochronous Gen Example
WSCC 9 bus from before, gen 3 dropping (85 MW)
  No infinite bus, gen 1 is modeled with an isochronous generator (PW ISOGov1 model)
Gen 2 is modeled with a TGOV1 governor
Case is wscc_9bus_ISOGOV

## Slide 5: Isochronous Gen Example
Graph shows the change in the mechanical output
Most of the change in MWs due to the loss of gen 3 is being picked up by gen 1. This would not work in a large system.

## Slide 6: Droop Control
To allow power sharing between generators the solution is to use what is known as droop control, in which the desired set point frequency is dependent upon the generator’s output
R is known as the regulation constant or droop; a typical value is 4 or 5%.
At 60 Hz and a 5% droop, each 0.1 Hz change would change the output by 0.1/(60*0.05)=
3.33%

## Slide 7: WSCC 9 Bus Droop Example
Assume the previous gen 3 drop contingency (85 MW), and that gens 1 and 2 have ratings of 500 and 250 MVA respectively and governors with a 5% droop. What is the final frequency (assuming no change in load)?
To solve the problem in per unit, all values need to be on a common base (100 MVA)

## Slide 8: WSCC 9 Bus Droop Example
The below graphs compare the mechanical power and generator speed; note the steady-state values match the calculated 59.66 Hz value
Case is wscc_9bus_TGOV1

## Slide 9: WSCC 9 Bus Droop Example: R=0.01
Changing to the droop to 0.01 results in less steady-state frequency error, but at the cost of a faster generator response

## Slide 10: Quick Interconnect Calculation
When studying a system with many generators, each with the same (or close) droop, then the final frequency deviation is
The online generator summation should only include generators that actually have governors that can respond, can move in the desired direction, and it does not take into account generators hitting their limits
The online generators do not include the contingency generator(s)

## Slide 11: Larger System Example (Prob 6.11)
As an example, consider the 37 bus, nine generator example from earlier; assume one generator with 42 MW is opened. The total MVA of the remaining generators is 1132. With R=0.05
Case is Bus37_TGOV1

## Slide 12: Frequency Response Measure
Source: wecc.biz/Reliability/Frequency%20Response%20Analysis%20-%20Dmitry%20Kosterev.pdf

## Slide 13: WECC Interconnection Performance
Source: wecc.biz/Reliability/Frequency%20Response%20Analysis%20-%20Dmitry%20Kosterev.pdf
Higher values are better!

## Slide 14: WECC Interconnect Frequency Response
Data for the four major interconnects is available from NERC; these are the values between points A and B
www.nerc.com/pa/RAPA/ri/Pages/InterconnectionFrequencyResponse.aspx

## Slide 15: Eastern Interconnect Frequency Response
www.nerc.com/pa/RAPA/ri/Pages/InterconnectionFrequencyResponse.aspx

## Slide 16: ERCOT Frequency Response
As expected, smaller grids have greater frequency sensitivity
www.nerc.com/pa/RAPA/ri/Pages/InterconnectionFrequencyResponse.aspx

## Slide 17: Frequency Response Definition
FERC defines in RM13-11: “Frequency response is a measure of an Interconnection’s ability to stabilize frequency immediately following the sudden loss of generation or load, and is a critical component of the reliable operation of the Bulk-Power System, particularly during disturbances and recoveries.”
Design Event for WECC is N-2 (Palo Verde Outage) not to result in under frequency load shed (UFLS) (59.5 Hz in WECC)
ERCOT requires 5% load shed at 59.3 Hz, 10% at 58.9 Hz, and 10% at 58.5 Hz
Source: wecc.biz/Reliability/Frequency%20Response%20Analysis%20-%20Dmitry%20Kosterev.pdf

## Slide 18: ERCOT May 15, 2003 event
On May 15, 2003 at 2:54 am both Comanche Peak nuclear units tripped due to breaker failure from a lightning strike
  Located by Glen Rose, SW of Fort Worth
  2275 MW gen tripped immediately, 1146 MW also tripped within seconds, and 775 MW about 43 seconds afterwards
  System frequency got down to 59.26 Hz
471 MW of high-set under frequency load tripped at 59.7 Hz, and 1549 MW tripped at 59.3
Image source: ERCOT TAC Meeting, June 4, 2003 Presentation at http://slideplayer.com/slide/4543302/

## Slide 19: Transient Stability Load Modeling
Load modeling is certainly challenging!
For large system models an aggregate load can consist of many thousands of individual devices
The load is constantly changing, with key diurnal and temperature variations
  For example, a higher percentage of lighting load at night, more air conditioner load on hot days
Load model behavior can be quite complex during the low voltages that may occur in transient stability
Testing aggregate load models for extreme conditions is not feasible – we need to wait for disturbances!

## Slide 20: Transient Stability Load Modeling
Traditionally load models have been divided into two groups
  Static: load is a algebraic function of bus voltage and sometimes frequency
  Dynamic: load is represented with a dynamic model, with induction motor models the most common
The simplest load model is a static constant impedance
  Has been widely used
  Allowed the Ybus to be reduced, eliminating essentially all non-generator buses
  Presents no issues as voltage falls to zero
  Is rapidly falling out of favor

## Slide 21: Induction Motor Models
Induction motors, both three phase and single phase, make up a very large percentage of the load
Term induction machine is used to indicate either generator or motor; most uses are as motors
Induction machines have two major components
  A stationary stator, which is supplied with an ac voltage; windings in stator create a rotating magnetic field
  A rotating rotor, in which an ac current is induced (hence the name)
Two basic design types based on rotor design
  Squirrel-cage: rotor consists of shorted conducting bars laid into magnetic material in a cage structure
  Wound-rotor: rotor has windings similar to stator, with slip rings used to provide external access to the rotor windings

## Slide 22: Torque-Speed Curves
To help understand the behavior of an induction machine it is useful to plot various values as a function of speed (or equivalently, slip)
  Solve the equivalent circuit for a specified terminal voltage, and varying values of slip
  Plot results
  Recall torque times speed = power
    Here speed is the rotor speed
  When using per unit, the per unit speed is just 1-s, so PE = TE(1-s)

## Slide 23: Induction Motor Example Torque-speed Curves
The below graph shows the torque-speed curve for this induction machine; note the high reactive power consumption on starting (which is why the lights may dim when starting a clothes dryer!)
From the graph you can see with a 100 MW load
(0.8 pu on the 125 MW base), the slip is about
0.025

## Slide 24: Induction Motor Classes
Four major classes of induction motors, based on application. Key values are starting torque, pull-out torque, full-load torque, and starting current
Image source: ecmweb.com/motors/understanding-induction-motor-nameplate-information
In steady-state the motor will operate on the right side of the curve at the point at which the electrical torque matches the mechanical torque
A: Fans, pumps machine tools
B: Similar to A
C: Compressors, conveyors
D: High inertia such as hoists

## Slide 25: Induction Motor Stalling
The maximum of the torque-speed curve varies with the square of the terminal voltage
When the terminal voltage decreases, such as during a fault, the mechanical torque can exceed the electrical torque
  This causes the motor to decelerate, perhaps quite quickly, with the rate proportional to its inertia
  This deceleration causing the slip to increase, perhaps causing the motor to stall with s=1, resulting in a high reactive current draw
  Too many stalled motors can prevent the voltage from recovering

## Slide 26: Motor Stalling Example
Using case WSCC_CIM5, which models the WSCC 9 bus case with 100% induction motor load
Change the fault scenario to say a fault midway between buses 5 and 7, cleared by opening the line
Results are for a 0.1 second fault
Usually motor load is much less than 100%

## Slide 27: Composite Load Model
Contains up to four motors or single phase induction motor models; also includes potential for solar PV

## Slide 28: Modeling Time Variation in Load
Different time varying composite model parameters are now being used
Example of varying composite load percentages over a day

## Slide 29: The Generator Dynamic Equations We Will Use
Example power system problem with differential algebraic equations (DAEs) is the classical synchronous generator connected to an infinite bus.
The two differential variables are and ; in practice dynamic models can have many more.
Generator Parameters
is the machine inertia constant (in seconds)
is the synchronous frequency (260)
is the mechanical torque (power being supplied by the prime mover)
is the generator internal voltage, as controlled by the excitation system
is the generator transient impedance
damping constant of the generator
Infinite Bus / System
The infinite bus is defined by a Thevenin equivalent with voltage
And reactance
These are the harder variables to get.

## Slide 30: Homework Problem 3
Using the swing equation: A 60 Hz generator is supplying 150 MW and 0 Mvar to an infinite bus (with 1.0 per-unit) through two parallel transmission lines. The per-unit transient reactance for the machine is j0.01, and its inertia constant is 4 seconds. Each transmission line has a per-unit impedance (with 100 MVA base) of j0.06. A fault occurs at time = 0 one-third of the way down one of the lines, closer to the generator than the infinite bus. Assume no damping. (Use and calculate 3 time steps.)
Euler’s method
Where

## Slide 31: Homework Problem 3
Using the swing equation: A 60 Hz generator is supplying 150 MW and 0 Mvar to an infinite bus (with 1.0 per-unit) through two parallel transmission lines. The per-unit transient reactance for the machine is j0.01, and its inertia constant is 4 seconds. Each transmission line has a per-unit impedance (with 100 MVA base) of j0.06. A fault occurs at time = 0 one-third of the way down one of the lines, closer to the generator than the infinite bus. Assume no damping. (Use and calculate 3 time steps.)
Euler’s method
Where

## Slide 32: Homework Problem 3
Using the swing equation: A 60 Hz generator is supplying 150 MW and 0 Mvar to an infinite bus (with 1.0 per-unit) through two parallel transmission lines. The per-unit transient reactance for the machine is j0.01, and its inertia constant is 4 seconds. Each transmission line has a per-unit impedance (with 100 MVA base) of j0.06. A fault occurs at time = 0 one-third of the way down one of the lines, closer to the generator than the infinite bus. Assume no damping. (Use and calculate 3 time steps.)
Euler’s method
Where

## Slide 33: Homework Problem 3
Before the fault
The generator is connected to a Thevenin equivalent with
Solve the circuit for the generator internal voltage,
Which will give you and initial value of :
Now consider steady-state, to get
And
Using the swing equation: A 60 Hz generator is supplying 150 MW and 0 Mvar to an infinite bus (with 1.0 per-unit) through two parallel transmission lines. The per-unit transient reactance for the machine is j0.01, and its inertia constant is 4 seconds. Each transmission line has a per-unit impedance (with 100 MVA base) of j0.06. A fault occurs at time = 0 one-third of the way down one of the lines, closer to the generator than the infinite bus. Assume no damping. Damping constant D=0.1.
Euler’s method
Where
1
+
_
E
+
_
j0.01
j0.06
j0.06
seconds
Initial values:

## Slide 34: Homework Problem 3
After the fault
The Thevenin equivalent changes.
Now rewrite the swing equation
Using the swing equation: A 60 Hz generator is supplying 150 MW and 0 Mvar to an infinite bus (with 1.0 per-unit) through two parallel transmission lines. The per-unit transient reactance for the machine is j0.01, and its inertia constant is 4 seconds. Each transmission line has a per-unit impedance (with 100 MVA base) of j0.06. A fault occurs at time = 0 one-third of the way down one of the lines, closer to the generator than the infinite bus. Damping constant D=0.1. (Use and calculate 3 time steps.)
Euler’s method
Where
seconds
1
+
_
E
+
_
j0.01
j0.06
j0.02
j0.04
t |  |  |  | 
0 | 0.0599 | 0 | 0 | 42.42472
0.025 | 0.0599 | 1.060618 | 1.060618 | 37.42668
0.05 | 0.086415 | 1.996285 | 1.996285 | 20.5337
0.075 | 0.136323 | 2.509627 | 2.509627 | -5.29749
0.1 | 0.199063 | 2.37719 | 2.37719 | -33.8722
0.125 | 0.258493 | 1.530385 | 1.530385 | -57.2027
0.15 | 0.296753 | 0.100318 | 0.100318 | -67.8329
t |  |  |  | 
0 | 0.0599 | 0 | 0 | 42.42472
0.025 | 0.0599 | 1.060618 | 1.060618 | 37.42668
0.05 | 0.086415 | 1.996285 | 1.996285 | 20.5337
0.075 | 0.136323 | 2.509627 | 2.509627 | -5.29749
0.1 | 0.199063 | 2.37719 | 2.37719 | -33.8722
0.125 | 0.258493 | 1.530385 | 1.530385 | -57.2027
0.15 | 0.296753 | 0.100318 | 0.100318 | -67.8329
Note: units is radians/second above synchronous
i.e. 2.5 represents 60+2.5/(2)=60.4 Hz