## Slide 1: ECEN 616, Spring 2025 Methods of Electric Power System Analysis
Prof. Adam Birchfield
Dept. of Electrical and Computer Engineering
Texas A&M University
abirchfield@tamu.edu
Class 8: Transmission Lines, Part 1

## Slide 2: Homework
Example 1 – Solve using analytical methods and numerical methods (Forward Euler, 2nd order Runge-Kutta, trapezoidal with companion circuit approach)
Read Dommel chapters 1-3, the Noda 2009 paper, Greenwood Chapter 5 (and reference Ch. 1-4)
By Feb. 20th, solve examples 2-7 analytically.
Read these two papers by Feb. 20th:
  J. R. Marti, "Accurate Modelling of Frequency-Dependent Transmission Lines in Electromagnetic Transient Simulations," in IEEE Transactions on Power Apparatus and Systems, vol. PAS-101, no. 1, pp. 147-157, Jan. 1982.
  A. Morched, B. Gustavsen and M. Tartibi, "A universal model for accurate calculation of electromagnetic transients on overhead lines and underground cables," in IEEE Transactions on Power Delivery, vol. 14, no. 3, pp. 1032-1038, July 1999.

## Slide 3: Transmission Line Characteristics
Multiple Conductors: Three phases, neutral wires, multiple circuits on the same tower or nearby towers, earth returns
Mutual inductances and capacitances
Overhead vs underground
Bundled conductors
Transposed or not
Segmented ground wires, periodic grounding
Sagging at midpoint between tower span
Frequency dependent parameters—introducing high degrees of nonlinearity
Skin effect

## Slide 4: Modeling Transmission Lines
Transmission lines are characterized by a distributed complex impedance matrix and an admittance matrix .
Both and are frequency-dependent
The first step in modeling transmission lines is being able to get and from the line configuration

## Slide 5: Conductor Input Data
Overhead conductor data
  Phase or neutral
  Horizontal position (relative)
  Vertical position (0 is considered earth)
  Radius
  DC resistance
  Bundling
  Sag
Underground conductor data
Ground resistivity and relative permeability
Line length
https://www.pscad.com/webhelp/ol-help.htm

## Slide 6: Conductor Sag
Conductor sag can be approximated by reducing the effective height of the conductor by a value 2/3 of the maximum sag.
h = height at midspan + 1/3 sag
Dommel

## Slide 7: Bundled Conductor Pictures
Photo Source: BPA and American Electric Power
The AEP Wyoming-Jackson Ferry 765 kV line uses 6-bundle conductors. Conductors in a bundle are at the same voltage!

## Slide 8: Bundling
Bundling can be handled one of two ways
(1) each conductor in the bundle can be separately modeled, then eliminated assuming the voltages are the same and current evenly split
(2) Use an equivalent radius GMR

## Slide 9: Transposition
Transposed lines can be handled in detail, by modeling the actual transposed sections (either by rotating the phases or changing the X, Y coordinates within the line model
It is also possible to make the assumption that lines are fully transposed, which results in perfectly symmetric and matrices, thus balanced operation
https://www.pscad.com/webhelp/ol-help.htm

## Slide 10: Underground Cables
Underground cables may have multiple concentric layers
Each layer has its own permittivity, permeability, and conductivity
Alternating conducting and insulating layers
https://www.pscad.com/webhelp/ol-help.htm

## Slide 11: Earth Return
Including the effect of the earth plane requires knowledge or assumptions about the ground’s electrical properties
One method is Carson’s method, which is fairly accurate for homogeneous earth
  It uses “images” of the conductors reflected across the ground plane
  Adds correction terms to R and X
There is a lot of uncertainty in ground properties
Details are in Dommel and other papers
Dommel

## Slide 12: Skin Effect
The basic calculations give R and L for dc conditions
Due to skin effect, R will be higher for higher frequencies, and L will be lower
Tables and formulas are given in Dommel to correct for these
In this figure (Dommel), the zero sequence values are affected more by the ground path

## Slide 13: Basic Equations
Transmission lines are basically characterized by a distributed complex impedance matrix and an admittance matrix .
Both are , where is the number of conductors (including neutrals), and are distributed along the length of the line.
Telegraphers' equations
Both and are frequency-dependent, asymmetric, full matrices

## Slide 14: Types of Line Modeling
PI model: ,
  Inductor + resistor in series, capacitor in shunt
  R, L, C values evaluated for single frequency
  Does not account for propagation delay
  Can work for very short lines and when only a narrow band of frequencies is important
Single Frequency, Constant Parameters
  Uses propagation delay, distributed-parameter model
  Also known as Bergeron Model
  Again, you must pick a single frequency for validity
Frequency-Dependent Model
  Approximates the nonlinear frequency dependence by calculating different models per frequency level

## Slide 15: Transmission Lines: Differential Section
Consider a two-terminal transmission line of length . Refer to the “sending end” as and the “receiving end” as . We’re interested in the sending and receiving end voltage and current, and
We define the distributed parameter line model as shown with
From circuit theory as

## Slide 16: Solving the Telegrapher’s Equations
These two equations are the telegrapher’s equations. We use the Fourier transform to convert time to frequency using the relation
where
where
The solutions have the general form in the frequency domain
Where and , and A and B are unknown constants
are all functions of frequency
Check that these solutions solve the differential equations

## Slide 17: Boundary Conditions
Eliminate A and B by solving for and , using the k and m terms defined on the prior page
After some algebra to eliminate A and B you get
Pause here. This is still an exact solution in the frequency domain, and we’ll come back here for frequency dependent models.
Remember and are functions of frequency

## Slide 18: Lossless Model in the Time Domain
For the lossless model, we assume , so and
So (which is a constant real number)
And , where
And for the equations we get
and
Convert to the time domain and get
where
where
This is exactly the lossless Bergeron model!

## Slide 19: Bergeron Model (Lossless, Single-Phase)
Line decouples due to propagation delay
Model line as Norton source on each end
Current source is constant and depends on voltage and current on other end of the line in the past
Where
https://www.pscad.com/webhelp/ol-help.htm
Where is the line length

## Slide 20: Bergeron Model, with Losses
The Bergeron model approximates losses by splitting the resistance (including resistance associated with ground earth return) into fourths
¼ at each end, ½ in the middle
Approximate the line as two lossless lines with ½ length each
Again, we require just one frequency