## Slide 1: ECEN 460, Spring 2026 Power System Operation and Control
Prof. Adam Birchfield
Dept. of Electrical and Computer Engineering
Texas A&M University
abirchfield@tamu.edu
Class 6: Transformers, Part 2

## Slide 2: Homework 3 and 4
No homework on generators. Make sure you understand the lecture notes and labs 2 and 3 (starting this week).
Homework 3 on transformers: book problems 3.4, 3.5, 3.23, due Feb. 3rd.
Homework 4 on transmission lines: book regular problems 4.10, 4.11, 4.20, and 4.41, 5.14 (a,b), 5.38, and 5.41 (a,b), due Feb. 10th.

## Slide 3: Non-Ideal Transformer Example
Example: A single phase, 15 MVA, 35/13 kV transformer has the following test data:
open circuit: 14 amps, with 3 kW losses
short circuit: 6 kV, with 200 kW losses
Determine the model parameters.
n

## Slide 4: Transformer Example, Cont’d
From the short circuit test
From the open circuit test

## Slide 5: Per Unit Change of MVA Base
Parameters for equipment are often given using power rating of equipment as the MVA base
To analyze a system all per unit data must be on a common power base

## Slide 6: Per Unit Change of Base Example
A 54 MVA transformer has a leakage reactance of 3.69%. What is the reactance on a 100 MVA base?

## Slide 7: Transformer Reactance
Transformer reactance is often specified as a percentage, say 10%. This is a per unit value (divide by 100) on the power base of the transformer.
Example: A 350 MVA, 230/20 kV transformer has leakage reactance of 10%. What is p.u. value on 100 MVA base? What is value in ohms (230 kV)?

## Slide 8: Three Phase Per-Unit
Procedure is very similar to 1 phase except we use a 3 phase VA base, and use line to line voltage bases
Pick a VA base for the entire system
Pick a voltage base for each different voltage level, . Voltages are line to line.
Calculate the impedance base
Exactly the same impedance bases as with single phase!

## Slide 9: Three Phase Per-Unit, Cont'd
Calculate the current base,
Convert actual values to per unit
Exactly the same current bases as with single phase!
But, be careful in using 3ph bases to calculate it (need a root 3)

## Slide 10: Three Phase Per-Unit Example
Solve for the current, load voltage and load power in the previous circuit, assuming a power base of 300 MVA, and line to line voltage bases of 13.8 kV,138 kV and 27.6 kV (square root of 3 larger than the 1f example voltages). Also assume the generator is Y-connected so its line to line voltage is 13.8 kV.
Convert to per unit
as before. Note the
system is exactly the
same!

## Slide 11: 3 Per-Unit Example, Cont'd
Again, analysis is exactly the same!

## Slide 12: 3 Per-Unit Example, Cont’d 2
Differences appear when we convert back to actual values

## Slide 13: 3 Per-Unit Example 2
Assume a load of 100+j50 MVA with of 69 kV is connected to a source through the below network:
What is the supply current and complex power?
Answer: I=467 amps, S = 103.3 + j76.0 MVA