## Slide 1: ECEN 460, Spring 2026 Power System Operation and Control
Prof. Adam Birchfield
Dept. of Electrical and Computer Engineering
Texas A&M University
abirchfield@tamu.edu
Class 12: The Power Flow Problem

## Slide 2: Announcements
Homework #5: book problems 6.30 and 6.31, due Thursday, Feb. 26, 2026
Homework #6: book problems 6.9, 6.12, 6.18, 6.25, 6.38, due Thursday, Mar 5, 2026

## Slide 3: Recall, Transmission Line and Transformer Models
Transmission lines use the "pi" model
Transformer non-ideal model is simplified with the per-unit system (and neglecting shunt elements)
These devices reduce down to impedances

## Slide 4: Recall, Building the Y-Bus Matrix
Here are the steps for building the Y-bus matrix
  Start with an NxN matrix of all zeros (N is the number of buses)
  For any shunt elements (connected to ground, such as most capacitors)
    Add to the corresponding diagonal elements of the Y-bus
  For branches between two buses,
    Add to both diagonal elements of the Y-bus
    Subtract from both off-diagonal elements of the Y-bus
We add one network element at a time to the Y-bus matrix!
Remember,

## Slide 5: The Power Flow Problem
What we know:
  Generator real power
  Generator voltage magnitude
  Load real and reactive power
What we don't know:
  Bus voltage angles
  Non-generator bus voltage magnitude
  Generator reactive power
  Current injections of generators or loads
Note that the problem is formulated with power values, not current, so we cannot use the Y-bus equations directly
Power flow problem is non-linear

## Slide 6: Example of a Non-Linear Problem
Solve for x:
Can solve analytically or iteratively
  Analytically: manipulate the algebra to attempt to isolate x and get a closed-form solution (possible but difficult here, may have hidden assumptions, impossible in some problems)
  Iteratively: make a guess at the answer and use a systematic updating technique to gradually improve the guess
    May converge or diverge
    Convergence depends on how good the initial guess is
    Two methods we will discuss: Gauss and Newton-Raphson
The analytical solution of this problem is

## Slide 7: Gauss Method
Method:
Write equation in implicit form x=h(x)
Make an initial guess of x,
For each iteration ,
When a fixed point is found such that , solution to original equation has been found

## Slide 8: Gauss Method 2
Method:
Write equation in implicit form x=h(x)
Make an initial guess of x,
For each iteration ,
When a fixed point is found such that , solution to original equation has been found
Solve
Guess
0 | 1
1 | 2
2 | 2.41421
3 | 2.55377
4 | 2.59805
5 | 2.61185
0 | 1
1 | 2
2 | 2.41421
3 | 2.55377
4 | 2.59805
5 | 2.61185
6 | 2.61612
7 | 2.61744
8 | 2.61785
9 | 2.61798
10 | 2.61802
11 | 2.61803
6 | 2.61612
7 | 2.61744
8 | 2.61785
9 | 2.61798
10 | 2.61802
11 | 2.61803

## Slide 9: Newton-Raphson Method
Method:
Write equation as f()=0
Make an initial guess of ,
For iteration , define
Write Taylor series expansion:
Approximate with only first two terms:
Solve for
Solve for new estimate of

## Slide 10: Newton-Raphson Method, example
Method:
Write equation as f()=0
Make an initial guess of ,
For iteration , define
Write Taylor series expansion:
Approximate with only first two terms:
Solve for
Solve for new estimate of
Solve
Guess

## Slide 11: Newton-Raphson Method, example 2
0 | 1
1 | 3.0000000000000000
2 | 2.6233096782319105
3 | 2.6180351744324595
4 | 2.6180339887499550
5 | 2.6180339887498950
6 | 2.6180339887498950
0 | 1
1 | 3.0000000000000000
2 | 2.6233096782319105
3 | 2.6180351744324595
4 | 2.6180339887499550
5 | 2.6180339887498950
6 | 2.6180339887498950
Solve
Guess

## Slide 12: Stopping Criteria
How many iterations do we go?
Choose a tolerance
Stop when , where
If is a vector (multi-variable problems), need to take the norm
Two common norms are the Euclidian & infinity

## Slide 13: Compare Gauss and Newton-Raphson
Gauss
  Relatively fast iterations, easy to calculate and program
  For power flow, requires programming complex numbers
  Convergence can be slower and unreliable
Newton-Raphson
  More complicated because it requires calculating the derivative
  Much better convergence: when close to solution, the error decreases quite quickly—method has quadratic convergence
Analytical solution:
=2.618033988749895
 | (Gauss) | (Newton Raphson)
0 | 1 | 1
1 | 2 | 3.0000000000000000
2 | 2.41421 | 2.6233096782319105
3 | 2.55377 | 2.6180351744324595
4 | 2.59805 | 2.6180339887499550
5 | 2.61185 | 2.6180339887498950
6 | 2.61612 | 2.6180339887498950
7 | 2.61744 | 
8 | 2.61785 | 
9 | 2.61798 | 
10 | 2.61802 | 
11 | 2.61803 | 
0 | 1 | 1
1 | 2 | 3.0000000000000000
2 | 2.41421 | 2.6233096782319105
3 | 2.55377 | 2.6180351744324595
4 | 2.59805 | 2.6180339887499550
5 | 2.61185 | 2.6180339887498950
6 | 2.61612 | 2.6180339887498950
7 | 2.61744 | 
8 | 2.61785 | 
9 | 2.61798 | 
10 | 2.61802 | 
11 | 2.61803 | 
After 4 iterations, error of Gauss is 0.02,
Error of Newton-Raphson is

## Slide 14: Multi-Variable Newton-Raphson
Next, we generalize to the case where is an n-dimension vector, and f(x)=0 is an n-dimensional function
Again, define
Taylor series for

## Slide 15: Jacobian Matrix
We can write the truncated Taylor series in Matrix form as the Jacobian matrix
So,
And so

## Slide 16: Multi-Variable Newton-Raphson Example
Solve for and such that

## Slide 17: Multi-Variable Newton-Raphson Example 2
Solve for and such that
First, symbolically determine the Jacobian Then Arbitrarily guess
Each iteration we check to see if it is below our specified tolerance

## Slide 18: Power Balance Equations
Current injection is given by the Y-bus formulation we have from before
For each bus i in the system, the power injection (generation – load) is thus
This is a complex equation. Next we want to convert it to a set of real equations for and

## Slide 19: Power Balance Equations, cont.
First, define and
And use
Resolve into real and imaginary parts:
Power balance equations

## Slide 20: Power Flow Problem Variables
These two equations must be satisfied for all buses in the system
Total of 2n equations
Parameters g and b are known from the Y-bus
Each bus has four variables:
  Bus voltage magnitude
  Bus voltage angle
  Bus real power injection
  Bus reactive power injection
So in general, we need to pre-specify 2 additional variables at each bus before we can solve

## Slide 21: Power Flow Bus Types
  Each bus has one of three basic types, and for each one there are two known variables and two unknown variables:
Load (PQ) bus
  Assume P/Q are fixed at most buses in the system
  Known: and , Unknown: and
Slack bus
  Only one in the whole system
  Usually assigned to a large generator bus
  Known: and , Unknown: and
  Provides angle reference () and picks up the slack P
Generator (PV) bus
  Other generators (5-10% of buses in a large system)
  Assume generator is controlling power output and voltage
  Known: and , Unknown: and