## Slide 1: ECEN 460, Spring 2026 Power System Operation and Control
Prof. Adam Birchfield
Dept. of Electrical and Computer Engineering
Texas A&M University
abirchfield@tamu.edu
Class 13: Newton-Raphson Solution Method for the Power Flow Problem

## Slide 2: Announcements
Homework #5: book problems 6.30 and 6.31, due Thursday, Feb. 26, 2026
Homework #6: book problems 6.9, 6.12, 6.18, 6.25, 6.38, due Thursday, Mar 5, 2026

## Slide 3: Recall, Transmission Line and Transformer Models
Transmission lines use the "pi" model
Transformer non-ideal model is simplified with the per-unit system (and neglecting shunt elements)
These devices reduce down to impedances

## Slide 4: Recall, Building the Y-Bus Matrix
Here are the steps for building the Y-bus matrix
  Start with an NxN matrix of all zeros (N is the number of buses)
  For any shunt elements (connected to ground, such as most capacitors)
    Add to the corresponding diagonal elements of the Y-bus
  For branches between two buses,
    Add to both diagonal elements of the Y-bus
    Subtract from both off-diagonal elements of the Y-bus
We add one network element at a time to the Y-bus matrix!
Remember,

## Slide 5: The Power Flow Problem
What we know:
  Generator real power
  Generator voltage magnitude
  Load real and reactive power
What we don't know:
  Bus voltage angles
  Non-generator bus voltage magnitude
  Generator reactive power
  Current injections of generators or loads
Note that the problem is formulated with power values, not current, so we cannot use the Y-bus equations directly
Power flow problem is non-linear

## Slide 6: Power Flow Problem Variables
These two equations must be satisfied for all buses in the system
Total of 2n equations
Parameters g and b are known from the Y-bus
Each bus has four variables:
  Bus voltage magnitude
  Bus voltage angle
  Bus real power injection
  Bus reactive power injection
So in general, we need to pre-specify 2 additional variables at each bus before we can solve

## Slide 7: Power Flow Bus Types
  Each bus has one of three basic types, and for each one there are two known variables and two unknown variables:
Load (PQ) bus
  Assume P/Q are fixed at most buses in the system
  Known: and , Unknown: and
Slack bus
  Only one in the whole system
  Usually assigned to a large generator bus
  Known: and , Unknown: and
  Provides angle reference () and picks up the slack P
Generator (PV) bus
  Other generators (5-10% of buses in a large system)
  Assume generator is controlling power output and voltage
  Known: and , Unknown: and

## Slide 8: Using Newton-Raphson to Solve the Power Flow Problem
Gauss is no longer in wide use for power flow solutions
Newton-Raphson is the standard method
Variables are and for every bus (except slack bus)

## Slide 9: Newton-Raphson Power Flow Procedure
Same procedure we have been using for N-R solutions so far
Build the Y-bus matrix
Write the list the variables and power balance equations
Make the power flow Jacobian
Make an initial guess of
While

## Slide 10: Power Flow Jacobian Matrix
The most difficult part of the algorithm is determining and inverting the n by n Jacobian matrix

## Slide 11: Power Flow Jacobian Matrix, Cont.
Jacobian elements are calculated by differentiating each function, ), with respect to each variable. For example, if is the bus i real power equation

## Slide 12: Power Flow Example #1
For the two bus power system shown below, use the Newton-Raphson power flow to determine the voltage magnitude and angle at bus two. Assume that bus one is the slack and SBase = 100 MVA.

## Slide 13: Power Flow Example #1

## Slide 14: Power Flow Example #1

## Slide 15: Power Flow Example #1, Solution
For the two bus power system shown below, use the Newton-Raphson power flow to determine the voltage magnitude and angle at bus two. Assume that bus one is the slack and SBase = 100 MVA.

## Slide 16: Power Flow Example #1, Solution Cont.