## Slide 1: ECEN 460, Spring 2026 Power System Operation and Control
Prof. Adam Birchfield
Dept. of Electrical and Computer Engineering
Texas A&M University
abirchfield@tamu.edu
Class 14: More Power Flow Examples

## Slide 2: Announcements
Homework #6: book problems 6.9, 6.12, 6.18, 6.25, 6.38, due Thursday, Mar 5, 2026

## Slide 3: The Power Flow Problem
What we know:
  Generator real power
  Generator voltage magnitude
  Load real and reactive power
What we don't know:
  Bus voltage angles
  Non-generator bus voltage magnitude
  Generator reactive power
  Current injections of generators or loads
Note that the problem is formulated with power values, not current, so we cannot use the Y-bus equations directly
Power flow problem is non-linear

## Slide 4: Power Flow Problem Variables
These two equations must be satisfied for all buses in the system
Total of 2n equations
Parameters g and b are known from the Y-bus
Each bus has four variables:
  Bus voltage magnitude
  Bus voltage angle
  Bus real power injection
  Bus reactive power injection
So in general, we need to pre-specify 2 additional variables at each bus before we can solve

## Slide 5: Power Flow Bus Types
  Each bus has one of three basic types, and for each one there are two known variables and two unknown variables:
Load (PQ) bus
  Assume P/Q are fixed at most buses in the system
  Known: and , Unknown: and
Slack bus
  Only one in the whole system
  Usually assigned to a large generator bus
  Known: and , Unknown: and
  Provides angle reference () and picks up the slack P
Generator (PV) bus
  Other generators (5-10% of buses in a large system)
  Assume generator is controlling power output and voltage
  Known: and , Unknown: and

## Slide 6: Newton-Raphson Power Flow Procedure
Same procedure we have been using for N-R solutions so far
Build the Y-bus matrix
Write the list the variables and power balance equations
Make the power flow Jacobian
Make an initial guess of
While

## Slide 7: Two Bus Solved Values
Once the voltage angle and magnitude at bus 2 are known we can calculate all the other system values, such as the line flows and the generator reactive power output

## Slide 8: Low Voltage Solution!
Red region converges to the high voltage solution, while the yellow region converges to the low voltage solution
This shows the region of convergence for different initial guesses of bus 2 angle (x-axis) and magnitude (y-axis)

## Slide 9: Generator Reactive Power Limits
The reactive power output of generators varies to maintain the terminal voltage; on a real generator this is done by the exciter
To maintain higher voltages requires more reactive power
Generators have reactive power limits, which are dependent upon the generator's MW output
These limits must be considered during the power flow solution
  During power flow, once a solution is obtained, check to make generator reactive power output is within its limits
  If the reactive power is outside of the limits, fix Q at the max or min value, and resolve treating the generator as a PQ bus
    this is know as "type-switching"
    also need to check if a PQ generator can again regulate
Rule of thumb: to raise system voltage we need to supply more vars

## Slide 10: Power Flow Example #2
Bus 1 contains a large generating unit operating at V=1.0 pu
Bus 2 has a load consuming 200 MW and 100 MVR
Bus 3 has a generator that is set to produce 30 MW and control its terminal voltage to 1.0 pu
Want to solve for all bus voltages and line flows

## Slide 11: Power Flow Example #2

## Slide 12: Power Flow Example #2

## Slide 13: Power Flow Example #2

## Slide 14: Power Flow Example #2

## Slide 15: Power Flow Example #2

## Slide 16: Power Flow Example #2, Solution
First, figure out bus types, knowns, and unknowns
Build Y-bus
Identify variables and equations (unknown , V and known P, Q)
Bus | Type | Known | Unknown
1 | Slack | , V | P, Q
2 | PQ | P, Q | , V
3 | PV | P, V | , Q
Bus | Type | Known | Unknown
1 | Slack |  | P, Q
2 | PQ | P, Q | 
3 | PV | P, V | 
Y-bus=

## Slide 17: Power Flow Example #2, Solution
Bus | Type | Known | Unknown
1 | Slack | , V | P, Q
2 | PQ | P, Q | , V
3 | PV | P, V | , Q
Bus | Type | Known | Unknown
1 | Slack |  | P, Q
2 | PQ | P, Q | 
3 | PV | P, V | 
Y-bus=;
Write out power balance equations to get f(x):
And the Jacobian from all the partial derivatives

## Slide 18: Power Flow Example #2, Solution
Iteration 1
Iteration 2
Iteration 3

## Slide 19: The N-R Power Flow: 5-Bus Example
400 MVA
15 kV
400 MVA
15/345 kV
T1
T2
800 MVA
345/15 kV
800 MVA
15 kV
520 MVA
80 MW
40 Mvar
280 Mvar
800 MW
Line 3 345 kV
Line 2
Line 1
345 kV 100 mi
345 kV 200 mi
50 mi
1
4
3
2
5
Single-line diagram

## Slide 20: The N-R Power Flow: 5-Bus Example
Table 1.
Bus input
data
Bus | Type | V per unit |  degrees | PG per unit | QG per unit | PL per unit | QL per unit | QGmax per unit | QGmin per unit
1 | Swing | 1.0 | 0 |  |  | 0 | 0 |  | 
2 | Load |  |  | 0 | 0 | 8.0 | 2.8 |  | 
3 | Constant voltage | 1.05 |  | 5.2 |  | 0.8 | 0.4 | 4.0 | -2.8
4 | Load |  |  | 0 | 0 | 0 | 0 |  | 
5 | Load |  |  | 0 | 0 | 0 | 0 |  | 
Table 2.
Line input data
Bus-to-Bus | R’ per unit | X’ per unit | G’ per unit | B’ per unit | Maximum MVA per unit
2-4 | 0.0090 | 0.100 | 0 | 1.72 | 12.0
2-5 | 0.0045 | 0.050 | 0 | 0.88 | 12.0
4-5 | 0.00225 | 0.025 | 0 | 0.44 | 12.0
Notes: 20

## Slide 21: The N-R Power Flow: 5-Bus Example
Table 3.
Transformer
input data
Bus-to-Bus | R per unit | X per unit | Gc per unit | Bm per unit | Maximum MVA per unit | Maximum TAP Setting per unit
1-5 | 0.00150 | 0.02 | 0 | 0 | 6.0 | —
3-4 | 0.00075 | 0.01 | 0 | 0 | 10.0 | —
Table 4. Input data
and unknowns
Bus | Input Data | Unknowns
1 | V1 = 1.0, 1 = 0 | P1, Q1
2 | P2 = PG2-PL2 = -8 Q2 = QG2-QL2 = -2.8 | V2, 2
3 | V3 = 1.05 P3 = PG3-PL3 = 4.4 | Q3, 3
4 | P4 = 0, Q4 = 0 | V4, 4
5 | P5 = 0, Q5 = 0 | V5, 5
Notes: 21

## Slide 22: Time to Close the Hood: Let the Computer Do the Math! (Ybus Shown)
Notes: 22

## Slide 23: Ybus Details
Elements of Ybus connected to bus 2
Notes: 23

## Slide 24: Here Are the Initial Bus Mismatches
Notes: 24

## Slide 25: And the Initial Power Flow Jacobian
Notes: 25

## Slide 26: And the Hand Calculation Details!
Notes: 26

## Slide 27: Five Bus Power System Solved
Notes: 27

## Slide 28: Five Bus System with Capacitor
A capacitor has been added at bus 2 to fix its low voltage

## Slide 29: Contingency Analysis
Contingency analysis provides an automatic way of looking at all the statistically likely contingencies. In this example the contingency set is all the single line and transformer outages
Notes: 29

## Slide 30: Power Flow Application - PJM Control Center