## Slide 1: ECEN 460, Spring 2026 Power System Operation and Control
Prof. Adam Birchfield
Dept. of Electrical and Computer Engineering
Texas A&M University
abirchfield@tamu.edu
Class 17: Economic Dispatch Examples

## Slide 2: Announcements
Homework #7: 6th edition book problems 6.62, 6.63, 6.65 or 7th edition book problems 7.1, 7.2, 7.4
  Due Tuesday, March 24th

## Slide 3: Economic Dispatch Summary
Minimize total generator cost, subject to serving total load
Each generator’s incremental cost curve is derivative of cost curve
Key necessary conditions for economic dispatch solution:
  Total generated power must equal load + losses
  Incremental cost for each generator (times penalty factor if losses are included) must be equal to the system .

## Slide 4: System Lambda and Generator Limits
When the ED problem is solved, part of the solution is the incremental cost in $/MWh. This would be the cost to serve one more MW of power. Higher is typical for a more constrained or higher-load situation.
Generators have limits on the minimum and maximum amount of power they can produce
  Often times the minimum limit is not zero. This represents a limit on the generator’s operation with the desired fuel type
  Because of varying system economics usually many generators in a system are operated at their maximum MW limits.
Each generator has an incremental cost
  If the generator's incremental cost is < , the generator should be operated at its maximum.
  If the generator's incremental cost is > , it should be operated at its minimum.
  Some generators may have their incremental cost = , these are the marginal units operated somewhere between minimum and maximum.

## Slide 5: Penalty Factors
The losses on the transmission system are a function of the generation dispatch. In general, using generators closer to the load results in lower losses
This impact on losses should be included when doing the economic dispatch, and can be done by using what are known as penalty factors
A penalty factor is multiplied by the generator cost to represent the effect of losses: i.e. a generator that increases the losses by operating has a penalty factor > 1.0
For Lab 6 we are looking at the effect of penalty factors

## Slide 6: Economic Dispatch Summary
Minimize total generator cost, subject to serving total load
Each generator’s incremental cost curve is derivative of cost curve
Key necessary conditions for economic dispatch solution:
  Total generated power must equal load + losses
  Incremental cost for each generator (times penalty factor if losses are included) must be equal to the system .

## Slide 7: System Lambda and Generator Limits
When the ED problem is solved, part of the solution is the incremental cost in $/MWh. This would be the cost to serve one more MW of power. Higher is typical for a more constrained or higher-load situation.
Generators have limits on the minimum and maximum amount of power they can produce
  Often times the minimum limit is not zero. This represents a limit on the generator’s operation with the desired fuel type
  Because of varying system economics usually many generators in a system are operated at their maximum MW limits.
Each generator has an incremental cost
  If the generator's incremental cost is < , the generator should be operated at its maximum.
  If the generator's incremental cost is > , it should be operated at its minimum.
  Some generators may have their incremental cost = , these are the marginal units operated somewhere between minimum and maximum.

## Slide 8: Economic Dispatch Problem, Example 1
A system has two generators with the following cost curves.
and are the generator costs, in $/hr
and are the generator real power outputs, in MW
Each generator must be dispatched within the following limits
If the total system load is 325 MW, what should be and to minimize the total system cost ?
Also, what is the incremental cost to supply 1 more MW? How does the solution change if the load goes up to 400 MW? Down to 250 MW? Up to 570 MW? Up to 750 MW?

## Slide 9: Economic Dispatch Problem, Example 1
Fundamental principle: For generators within their limits, the incremental cost should be equal to the system marginal cost
So we basically have two equations: We need to meet the load
And we need the incremental cost (derivatives) to be equal
Take the derivatives to find the incremental cost
Solving, we get

## Slide 10: Economic Dispatch Problem, Example 1
Now try with the other values of the load
  For load of 400 MW, you get
  For load of 250 MW, you get
  For load of 570 MW, you get
  For load of 750 MW, you get
But wait a minute, check the limits
  In the first case, we are fine, no limit violations
  In the second case, will be stuck at its min limit, , ,
  In the third case, will be stuck at its max limit, , ,
  In the fourth case, we have a problem!!
Note that lambda and the incremental cost are related in this way

## Slide 11: Worksheet -- Economic Dispatch, Exercise 2
Four generators with the following cost equations and limits:
Two parts to this question:
Make a table with five values of (system marginal cost): 9, 12, 15, 18, 21 $/MWh. Calculate and total system P for each of these ’s. (Remember, for each generator i not at a limit.)
If we want to serve a total of 500 MW of load, what is the optimal dispatch (), the system marginal cost , and total cost?

## Slide 12: Economic Dispatch, Exercise 2
($/MWh) |  |  |  |  | 
9 |  |  |  |  | 
12 |  |  |  |  | 
15 |  |  |  |  | 
18 |  |  |  |  | 
21 |  |  |  |  | 
9 |  |  |  |  | 
12 |  |  |  |  | 
15 |  |  |  |  | 
18 |  |  |  |  | 
21 |  |  |  |  |